## Methodology
The EA require all raw overflow event data to be passed through a spill counting tool. This transposes the data into the 12/24 spill counting methodology. The standard 12/24 spill counting approach defined by the EA is as follows:
• Spill counting starts when the first discharge occurs.
• Any discharge(s) in the first 12 hour block is counted as 1 spill.
• Any discharge(s) in the next and subsequent 24 hour blocks are each counted as 1 additional spill per block.
• This counting continues until there is a 24 hour block with no discharge.
• For the next discharge after the 24 hour block with no discharge, the 12 hour and 24 hour block spill counting sequence begins again.
The graph below illustrates application of 12/24 spill counting to real level data, with the start points of 12- and 24-hour blocks being determined by when recorded level exceeds an overflow threshold. The data in chart below shows a total of nine 12/24 spills counted.

## EDM Return for Anglian Water
EDM Return for Anglian Water Annual 2020
Period selected from 01/01/2020 to 31/12/2020
Water Company Name | Site Name | Permit No. | Activity Reference (if more than one discharge) on permit | Shellfishery (Only populate for storm overflows that have Shellfish water EDM requirements) | Bathing Beach (Only populate for storm overflows that have bathing water EDM requirements) | Total Duration (hours) of all spills prior to processing through 12-24 hour counting method | Counted spills using 12-24hr counting method | % of reporting period EDM operational | Comments
Anglian Water | ABTHORPE TPS | AW1NF947/V001 | CSO | N/a | N/a | 0.5 | 2 | 100%
Anglian Water | ANWICK-RIVER LA TPS | ANNNF3244/13375/V001 | CSO | N/a | N/a | 309.25 | 37 | 100%
Anglian Water | ARRINGTON STW | ASCNF176/10117 | CSO | N/a | N/a | 59.5 | 23 | 99.99%
Anglian Water | ASHTON STW | AW1NF1362/V002 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | ATTLEBOROUGH-NORWICH RD #2 SP | AECNF782/11045/V001 | CSO | N/a | N/a | 36 | 3 | 100%
Anglian Water | Austin Field PS | AECTS189/10313/V001 | CSO | N/a | N/a | 11.5 | 13 | 100%
Anglian Water | BADWELL ASH STW | ASCNF2/10277/V002 | CSO | N/a | N/a | 1121.5 | 67 | 99.92% | Under investigation
Anglian Water | BARRINGTON-SLID LA #2 OV | AW1NF1380/V001 | CSO | N/a | N/a | 16 | 4 | 99.78%
Anglian Water | Beccles - Common Lane North TPS | ASETS16674/V001 | CSO | N/a | N/a | 85.5667 | 21 | 100%
Anglian Water | BEDFORD STW | AW1NF2460/V004 | CSO | N/a | N/a | 176.75 | 24 | 99.94%
Anglian Water | BELAUGH STW | AW4TF/351/V002 | CSO | N/a | N/a | 327.25 | 28 | 100%
Anglian Water | BENFLEET-MARSH TPS | AW2NFE08669/V001 | CSO | N/a | N/a | 56.5 | 11 | 100%
Anglian Water | BENFLEET STW | CSSC.4458/V001 | CSO | N/a | N/a | 243 | 34 | 100%
Anglian Water | BENHALL STW | ASENF2052/V001 | CSO | N/a | N/a | 23.25 | 4 | 100%
Anglian Water | BIGGLESWADE DARK LANE SSO | AWCNF11839/V001 | CSO | N/a | N/a | 21.5 | 25 | 99.97%
Anglian Water | BIGGLESWADE-SHORTMEAD ST TPS | AWCNF10469A | CSO | N/a | N/a | 188.75 | 13 | 100%
Anglian Water | Boston - Church Rd sp | AW3NFF988/V001 | CSO / EO | West Wash | N/a | 9.5667 | 4 | 99.73%
Anglian Water | Boston - East Side TPS | AW3TSF904/V002 | CSO | West Wash | N/a | 229.1 | 39 | 100%
Anglian Water | Boston - Fenside Rd sp | ANNNF4086/13728/V001 | CSO / EO | West Wash | N/a | 0.16667 | 3 | 99.99%
Anglian Water | Boston - London Rd PS | ANNNTS4084/13726/V001 | CSO / EO | West Wash | N/a | 0 | 0 | 36.35% | Under investigation
Anglian Water | Boston - London Rd sp (south forty foot drain) | AW3NFF987/V001 | CSO / EO | West Wash | N/a | 0 | 0 | 0% | Changed to alternative monitor position, now resolved
Anglian Water | Boston - Norfolk Place CSO | ANNTS4089/1373/V001 | CSO | West Wash | N/a | 3.5 | 10 | 100%
Anglian Water | Boston - Norfolk Street | ANNNF/4096/13733/V001 | CSO | West Wash | N/a | 2.5 | 18 | 100%
Anglian Water | Boston - Queens Rd | AWNNF1758/V001 | CSO | West Wash | N/a | 5.5333 | 1 | 23.06% | Changed to alternative monitor position, now resolved
Anglian Water | Boston - Sleaford Rd sp | ANNNF4085/13727/V001 | CSO / EO | West Wash | N/a | 9.3667 | 15 | 100%
Anglian Water | BOTTISHAM STW | AW1NF302/V003 | CSO | N/a | N/a | 1.75 | 5 | 99.25%
Anglian Water | BRADFIELD-MAYPOLE GREEN PS | AW1NF1275/V001 | CSO | N/a | N/a | 141.5 | 15 | 100%
Anglian Water | Bradwell Waterside TPS | ASENF2698A | CSO | N/a | N/a |  |  |  | NPS have not yet issued a CSO condition under TDC project
Anglian Water | BRANDON STW | AW1NF939/V003 | CSO | N/a | N/a | 1.75 | 1 | 100%
Anglian Water | BRAUNSTON STW | AW5NF694/V002 | CSO | N/a | N/a | 96.25 | 35 | 100%
Anglian Water | Brigg - Gas House Lane TPS | ANNNF956v001 | CSO | N/a | N/a | 1.7 | 6 | 100%
Anglian Water | Brigg STW - settled storm | AW3NFF892/V001 | CSO | N/a | N/a | 21.4 | 11 | 100%
Anglian Water | Brightlingsea overflow (Bellfld 35) | ASENF3270/12163/V001 | CSO | Colne | N/a | 7.7 | 24 | 100%
Anglian Water | Brightlingsea overflow - lower park OV | ASENF3270/12162/V001 | CSO | Colne | N/a | 4182.6333 | 187 | 100% | Reporting logic resolved
Anglian Water | Brightlingsea overflow - Station road #58 | ASENF32702/12166/V001 | CSO | Colne | N/a | 3.6 | 12 | 99.99%
Anglian Water | Brightlingsea overflow (western rd) community centre | ASENF3270/12167/V001 | CSO | Colne | N/a | 0.26667 | 4 | 96.91%
Anglian Water | Brightlingsea - Spring Rd CSO | ASENF3270/12165/V001 | CSO | Colne | N/a | 0.033333 | 1 | 100%
Anglian Water | Brightlingsea - West Dyke TPS (LWR PARK RD) CSO/EO | ASENF3284/12161/V001 | CSO / EO | Colne | N/a | 250.4667 | 43 | 100% | SOAF investigation (Storm Overflow Assesment Framework) with EA agreement in progress
Anglian Water | BROUGHTON-TOWNHILL(MH4103) | ANNNF3685/13537/V001 | CSO | N/a | N/a | 0 | 0 | 75.69% | Operational issue now resolved
Anglian Water | BUCKINGHAM TOWN SP | AWCNF579/10471/V001 | CSO | N/a | N/a | 24.75 | 2 | 100%
Anglian Water | BUCKINGHAM- WEST STREET SSO | AWCNF1604/V003 | CSO | N/a | N/a | 0 | 0 | 99.99%
Anglian Water | BUNGAY-BOYSCOTT LA SP | ASENF3927/15570/V001 | CSO | N/a | N/a | 2.5 | 3 | 100%
Anglian Water | BUNGAY-EARSHAM STREET SSO | AW4NF1774/V001 | CSO | N/a | N/a | 408.25 | 35 | 99.97%
Anglian Water | BUNGAY NETHERGATE ST CSO | ASENF 3930/15588/V001 | CSO | N/a | N/a | 12.75 | 18 | 99.93%
Anglian Water | BUNGAY-ST JOHNS ROAD SSO | AW4NF1773/V001 | CSO | N/a | N/a | 0.75 | 3 | 99.95%
Anglian Water | Burnham Market STW SO | AEENF1265/V004 | CSO | Burnham Overy Creek | N/a | 413.3667 | 115 | 100% | Catchment investigation underway
Anglian Water | BURNHAM ON CROUCH STW - storm sewage | ASETS10533/V002 | CSO | N/a | N/a | 1274 | 81 | 100% | Possible SOAF investigation (Storm Overflow Assesment Framework) with EA agreement
Anglian Water | BUXTON-COLTISHALL RD TPS | AEENF2225/V003 | CSO | N/a | N/a | 8.75 | 8 | 83.84% | Operational issue now resolved
Anglian Water | BYLAUGH-NEAR CHURCH STW | AW4NF/624/V004 | CSO | N/a | N/a | 78.25 | 10 | 98.79%
Anglian Water | CAISTER-HEADWORKS PS | AEENF3662/12406/V001 | CSO | N/a | N/a | 55.5 | 26 | 99.97%
Anglian Water | CAISTER - PUMP LANE STW | AEECS12404/V002 | CSO | N/a | N/a | 435.75 | 61 | 73.76% | Operational issue now resolved
Anglian Water | CAISTOR STW | AW3NFF232/V003 | CSO | N/a | N/a | 2442.5 | 120 | 100% | SOAF investigation (Storm Overflow Assesment Framework) with EA agreement in progress
Anglian Water | Cambridge - Riverside 187 SSO | AWCNF11361/V001 | CSO | N/a | N/a | 9.8333 | 4 | 98.82%
Anglian Water | Cambridge STW - storm sewage and settled storm | ASCNF1033/V003 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | CANVEY-FURTHERWICK RD SP | AW2NFE11984/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | CANVEY ISLAND STW | B.794/V001 | CSO | N/a | N/a | 6397.75 | 331 | 100% | Possible SOAF investigation (Storm Overflow Assesment Framework) with EA agreement
Anglian Water | CANVEY-NEW RD SP | ASETS2493/V003 | CSO | N/a | N/a | 60 | 5 | 100%
Anglian Water | CANVEY-POINT RD SP | ASETS16193/V001 | CSO | N/a | N/a | 9.25 | 3 | 100%
Anglian Water | CASTLE PT HIGH RD/SOUTHVIEW RD | EPR/NB3199AR/V001 | CSO | N/a | N/a | 0.5 | 1 | 100%
Anglian Water | CHELMSFORD-BUTTS WAY SP | ASENF540/10378/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | CHELMSFORD-GALLEYWOOD RD SP | AEENF3926/15628/V001 | CSO | N/a | N/a | 25.5 | 8 | 95.65%
Anglian Water | CHELMSFORD-N MLBN CHIGNAL R SP | ASENF2502/V003 | CSO | N/a | N/a | 3.25 | 2 | 100%
Anglian Water | CHELMSFORD STW | AW2TSE9961/V001_<1557l/s | CSO | N/a | N/a | 121.5 | 15 | 100%
Anglian Water | CHELMSFORD STW | AW2TSE9961/V001_>1557l/s | CSO | N/a | N/a | 315.25 | 32 | 100%
Anglian Water | Clacton 23 Park Square, Jaywick | ASENF3333/12237/V001 | CSO | N/a | Jaywick | 14.6333 | 9 | 100%
Anglian Water | Clacton - Collingwood Road / Wash Lane CSO | ASECS12233/V001 | CSO | N/a | Clacton Groyne 41/Clacton Martello Tower | 0.1 | 2 | 100%
Anglian Water | Clacton Golf Green Rd, Jaywick | ASETS3332/12240/V001 | CSO | N/a | Jaywick | 2.2 | 8 | 98.64%
Anglian Water | Clacton - Kings Parade/Hazlemere Road CSO (CLARENDON/HOLLAND OV) | ASECS3328/12234/V001 | CSO | N/a | Clacton | 0 | 0 | 100%
Anglian Water | Clacton - Martello Tower Pumping Station | ASECS3330/12236/V001 | CSO | N/a | Clacton Martello Tower | 0.2 | 2 | 98.8%
Anglian Water | Clacton - Park Road/Vicarage Road CSO | ASECS3326/12232/V001 | CSO | N/a | Clacton Groyne 41/Clacton Martello Tower | 0.033333 | 1 | 99.99%
Anglian Water | Clacton Seafront CSO/Gunfleet | ASECS3324/12230/V001 | CSO | N/a | Clacton | 0 | 0 | 100%
Anglian Water | Clacton STW Storm & EO | AEECS12401 /V005 | CSO | N/a | Holland | 428.5333 | 90 | 99.99% | Possible SOAF investigation (Storm Overflow Assesment Framework) with EA agreement
Anglian Water | Clacton - Victoria Road outfall | AW2CS662/V001 | CSO | N/a | Clacton | 0.23333 | 5 | 97.68%
Anglian Water | Clacton - West Road TPS | ASECS3325/12231/V001 | CSO | N/a | Clacton Martello Tower | 4.2 | 4 | 100%
Anglian Water | Cliff Quay new tunnel (Ipswich tunnel outfall) | ASETS3276/12156/V001 | CSO | N/a | N/a | 9.8 | 28 | 99.98%
Anglian Water | CLOPHILL WORKS SP | AWCNF11064/V001 | CSO | N/a | N/a | 16 | 7 | 100%
Anglian Water | COGGESHALL-EAST ST R O #18 OV | AW2NFE02579/V001 | CSO | N/a | N/a | 0 | 0 | 97.85%
Anglian Water | COLCHESTER-EAST BAY MAIN INT | AW2TSE03384/V001 | CSO | N/a | N/a | 3.25 | 7 | 99.97%
Anglian Water | COLCHESTER-HAVEN RD OV | ASETS4123/19243/V001 | CSO | N/a | N/a | 15.25 | 12 | 99.97%
Anglian Water | Colchester - Hunting Gate CSO | ASETS4124/19244/V001 | CSO | Colne, Pyfleet | N/a | 0.43333 | 4 | 93.66%
Anglian Water | Colchester - Hythe Bridge | AW2TSE00863/V001 | CSO | Colne, Pyfleet | N/a | 17.7333 | 8 | 94.15%
Anglian Water | Colchester - Rowhedge Albion St CSO | ASETS15689/V001 | CSO | Colne | N/a | 0.36667 | 4 | 98.75%
Anglian Water | Colchester - Rowhedge Regent Court CSO | ASETS3961/15688/V001 | CSO | Colne | N/a | 107.4667 | 22 | 100%
Anglian Water | Colchester - Royal London Middleborough EO | ASENF19245/4125/V001 | EO | Colne, Pyfleet | N/a | 0 | 0 | 0% | Under investigation
Anglian Water | COLCHESTER-SPRING LA OV | ASENF3627/12396/V001 | CSO | N/a | N/a | 111.5 | 18 | 100%
Anglian Water | Colchester - St Albans Rd CSO | ASENF4126/19246/V001 | CSO | Colne, Pyfleet | N/a | 135.9333 | 28 | 91.21%
Anglian Water | Colchester STW Settled Storm | ASETS1046/V001 | CSO | Colne, Pyfleet | N/a | 1619.3667 | 81 | 100% | Possible SOAF investigation (Storm Overflow Assesment Framework) with EA agreement
Anglian Water | COLD NORTON-STOW RD SP | ASENF2637/V003 | CSO | N/a | N/a | 185.5 | 27 | 100%
Anglian Water | COMBS FORD-COMBS FORD TPS | AW4NF808X/V001 | CSO | N/a | N/a | 26.25 | 6 | 100%
Anglian Water | CONINGSBY STW | ANNNF/1049/V001 | CSO | N/a | N/a | 1208.5 | 95 | 100% | SOAF investigation (Storm Overflow Assesment Framework) with EA agreement in progress
Anglian Water | CORBY-STUDFALL AVENUE SSO | AW5NF463/V001 | CSO | N/a | N/a | 8.5 | 2 | 100%
Anglian Water | CORTON-BAKERS SCORE PS, Corton, Lowestoft, Suffolk | ASETS2120/V001 | CSO | N/a | N/a | 37.5 | 20 | 99.98%
Anglian Water | CORTON-CHURCH LANE SM | ASECS3949/15627/V001 | CSO | N/a | N/a | 2.5 | 3 | 99.95%
Anglian Water | COSGROVE-DOGSMOUTH SO SSO | AWCNF3754/11624/V001 | CSO | N/a | N/a | 426.5 | 53 | 100%
Anglian Water | COTTON VALLEY STW | AWCNF10296/V002 | CSO | N/a | N/a | 115.25 | 10 | 100%
Anglian Water | Cromer STW | AEECS3749/V001 | CSO | N/a | N/a | 1219.1333 | 154 | 100% | Operational issue now resolved
Anglian Water | Cromer West Beach Sewage Tank (PROMENADE TPS) | AEECS868/12071/V001 | CSO | N/a | Cromer | 0.26667 | 2 | 100%
Anglian Water | CROWFIELD SP | AW1NF809/V001 | CSO | N/a | N/a | 390.5 | 41 | 100%
Anglian Water | DEANSHANGER SO SSO | AWCNF1627/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | DEDHAM STW | ASENF1055/V003 | CSO | N/a | N/a | 1033.5 | 61 | 100% | Scaling adjusted
Anglian Water | DENFORD SP | AWCNF1572/V001 | CSO | N/a | N/a | 70.75 | 12 | 100%
Anglian Water | DESBOROUGH-HILLTOP AVENUE SSO | AWNNF3994/13660/V001 | CSO | N/a | N/a | 16.75 | 7 | 100%
Anglian Water | DESBOROUGH-NEAR CORSET FACTO | AWNNF4112/13851/V001 | CSO | N/a | N/a | 21.75 | 33 | 98.8%
Anglian Water | DESBOROUGH-RECTORY FIELD SSO | AW5NF1888/V001 | CSO | N/a | N/a | 27.75 | 17 | 100%
Anglian Water | DESBOROUGH-RUSHTON RD SSO | AW5NF1887/V001 | CSO | N/a | N/a | 3.25 | 11 | 99.99%
Anglian Water | DESBOROUGH SP | AW5NF689/V001 | CSO | N/a | N/a | 53.25 | 23 | 100%
Anglian Water | DISS-SARACENS HD MOUNT ST OV | AEENF91766/10175/V001 | CSO | N/a | N/a | 2 | 4 | 99.99%
Anglian Water | DISS STW | AW4NF/625/V004 | CSO | N/a | N/a | 213.75 | 54 | 98.58%
Anglian Water | DOVERCOURT-LOW RD SP | AW2NF382/V001 | CSO | N/a | N/a | 53.75 | 58 | 100%
Anglian Water | DOWNHAM MARKET-DENIS SNZM SSO | AECNF259/10445/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | DOWNHAM MARKET-RAILWAY SSO | AECNF256/10443/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | DOWNHAM MKT-LYNN ROAD OV | AECNF260/10446/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | DRAUGHTON STW | AW5NF5221/V002 | CSO | N/a | N/a | 2217.5 | 118 | 100% | Operational issue resolved, under further investigation
Anglian Water | EARLS BARTON TPS | AWCNF2266/V003 | CSO | N/a | N/a | 65.5 | 37 | 100%
Anglian Water | East Runton - Beach Rd TPS | AEECS12197/V002 | CSO | N/a | N/a | 7.5 | 5 | 99.99%
Anglian Water | ELTON STW | AWNNF955/13141/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | Ely - Lisle lane | AECNF203/10401/V001 | CSO | N/a | N/a | 1.7333 | 14 | 95.25%
Anglian Water | Ely New STW - settled storm | AWCNF11352/V002 | CSO | N/a | N/a | 3985 | 168 | 65.52% | Changed to alternative monitor type, now resolved
Anglian Water | Ely Old STW - settled storm | AW1NF1176/V001 | CSO | N/a | N/a | 94.5667 | 88 | 91.65% | Changed to alternative monitor position, now resolved
Anglian Water | ELY-WALSINGHAM WAY OV | AECNF204/10402/V001 | CSO | N/a | N/a | 25.25 | 28 | 99.99%
Anglian Water | Ely - Willow Walk TPS | AECNF3110/11328/V001 | CSO | N/a | N/a | 0.16667 | 1 | 100%
Anglian Water | E TILBURY-BATA(LINFORD) TPS | AW2NFE00981/V001 | CSO | N/a | N/a | 27 | 4 | 100%
Anglian Water | FAKENHAM-NORWICH ROAD OV | AEENF889/12045/V001 | CSO | N/a | N/a | 4 | 10 | 100%
Anglian Water | FAKENHAM STW (OLD AND NEW) | AEENF3904/15448/V001 | CSO | N/a | N/a | 506.75 | 39 | 100%
Anglian Water | FELTWELL STW | AW1NF213/V002 | CSO | N/a | N/a | 1003.75 | 61 | 100% | SOAF investigation (Storm Overflow Assesment Framework) with EA agreement in progress
Anglian Water | FISH DOCKS PS, Humber Bridge Road, Grimsby | ANNTS4114/13404/V001 | CSO | N/a | N/a | 85.75 | 74 | 99.95% | Possible SOAF investigation (Storm Overflow Assesment Framework) with EA agreement
Anglian Water | FISHTOFT STW | ANNNF1069/V001 | CSO | N/a | N/a | 2.75 | 4 | 98.57%
Anglian Water | FORNHAM ALL SAINTS STW | AW1NF545/V003 | CSO | N/a | N/a | 199 | 16 | 100%
Anglian Water | Frinton on sea - Ashlyn's Road SPS | AW2NFE08784/V001 | CSO | N/a | Frinton | 27.8333 | 9 | 100%
Anglian Water | Frinton on sea - Esplanade/Second Ave CSO | ASECS3309/12191/V001 | CSO | N/a | Frinton | 0.83333 | 11 | 99.61%
Anglian Water | Frinton on sea - First Avenue | ASENF3683/12382/V001 | CSO | N/a | Frinton | 15.5 | 5 | 100%
Anglian Water | Frinton on sea - Holland Rd/Second Ave CSO | ASENF3310/12192/V001 | CSO | N/a | Frinton | 20.6333 | 10 | 100%
Anglian Water | Frinton on sea - Queens Road/Esplanade CSO | ASECS3311/12194/V001 | CSO | N/a | Frinton | 0.16667 | 2 | 100%
Anglian Water | Frinton - Upper Second Avenue - The Close | ASENF3684/12381/V001 | CSO | N/a | Frinton | 44.3667 | 54 | 100% | Proposed SOAF investigation (Storm Overflow Assesment Framework) with EA agreement
Anglian Water | GODMANCHESTER-WHITE HART TPS | AW1NF/2281/V001 | CSO | N/a | N/a | 0.75 | 2 | 100%
Anglian Water | Goldhanger - Fish Street SPS | AW2NFE10884/V001 | EO | Osea Island | N/a | 0 | 0 | 63.83% | Changed to alternative monitor, now resolved
Anglian Water | GREAT BILLING STW | AWNNF/13052/V003 | CSO | N/a | N/a | 574 | 111 | 100% | Proposed SOAF investigation (Storm Overflow Assesment Framework) with EA agreement
Anglian Water | GREAT CHESTERFORD STW | AWCNF3195/11340/V001 | CSO | N/a | N/a | 3 | 6 | 100%
Anglian Water | Great Wakering - Seaview Est SP | AW2NFE07169/V001 | CSO / EO | Foulness | N/a | 1.0333 | 2 | 99.97%
Anglian Water | Great Yarmouth - Boundary Road Storm PS | AEETS3291/12173/V001 | CSO | N/a | Great Yarmouth South | 1.1667 | 6 | 100%
Anglian Water | GT BADDOW HIGH ST/TABORS HL OV | ASENF3033/12078/V001 | CSO | N/a | N/a | 2.75 | 3 | 100%
Anglian Water | GT BENTLEY-THORRINGTON RD SP | ASENF563/10407/V001 | CSO | N/a | N/a | 215 | 42 | 100%
Anglian Water | GT BRINGTON SP | AW5NF5255/V001 | CSO | N/a | N/a | 205 | 36 | 100%
Anglian Water | GT WALDINGFIELD-FOLLEY RD SP | ASENF2370/V003 | CSO | N/a | N/a | 100.25 | 9 | 100%
Anglian Water | Gt Yarmouth - Bryants Quay CSO | AEETS3290/12175/V001 | CSO | N/a | Great Yarmouth Pier/Great Yarmouth South | 126.3 | 96 | 99.96% | Catchment investigation underway
Anglian Water | Gt Yarmouth-Gorleston - Gt Yarmouth Brush Bend | AEETS/3292/12178/V001 | CSO | N/a | Gorleston Beach | 26.3667 | 18 | 100%
Anglian Water | HALESWORTH STW | ASENF1286C | CSO | N/a | N/a | 458 | 42 | 100%
Anglian Water | HALVERGATE-MARSH RD SP | AW4NF928X/1 | CSO | N/a | N/a | 29.25 | 7 | 100%
Anglian Water | HARLAXTON STW | ANNNF1093/V002 | CSO | N/a | N/a | 1604.25 | 79 | 100% | SOAF investigation (Storm Overflow Assesment Framework) with EA agreement in progress
Anglian Water | HARPOLE-WEEDON RD SSO | AW5NF/1878/V001 | CSO | N/a | N/a | 2128.5 | 107 | 99.99% | SOAF investigation (Storm Overflow Assesment Framework) with EA agreement in progress
Anglian Water | HARWICH AND DOVERCOURT STW | ASETS/996/12050/V001_CSO | CSO | N/a | N/a | 56 | 21 | 100%
Anglian Water | HARWICH AND DOVERCOURT STW | ASETS/996/12050/V001_SSO | CSO | N/a | N/a | 30 | 38 | 100%
Anglian Water | HASLINGFIELD-STW | ASCNF1094/V001 | CSO | N/a | N/a | 428.25 | 49 | 100%
Anglian Water | Hatfield Peverel Crabbs Hill TPS | ASENF915/12034/V001 | CSO | N/a | N/a | 0.5 | 2 | 99.6%
Anglian Water | HAVERHILL STW | AW2NF342/V005 | CSO | N/a | N/a | 10.25 | 10 | 99.99%
Anglian Water | HIGHAM FERRERS-NORTHAMPTON RD | AWNNF4105/13857/V001 | CSO | N/a | N/a | 21.75 | 31 | 100%
Anglian Water | HITCHIN-BANCROFT REC SSO | AW1NF1886/V001 | CSO | N/a | N/a | 0 | 0 | 99.99%
Anglian Water | HITCHIN STW | AW1NF2464/V004_CSO | CSO | N/a | N/a | 4981.75 | 223 | 100% | Proposed SOAF investigation (Storm Overflow Assesment Framework) with EA agreement
Anglian Water | HITCHIN STW | AW1NF2464/V004_SSO | CSO | N/a | N/a | 3.75 | 4 | 100% | Proposed SOAF investigation (Storm Overflow Assesment Framework) with EA agreement
Anglian Water | HOLBEACH STW | AW5NF/378/V001 | CSO | N/a | N/a | 324.5 | 52 | 100% | Proposed SOAF investigation (Storm Overflow Assesment Framework) with EA agreement
Anglian Water | HOLCOT PS | AWNNF2385A | CSO | N/a | N/a |  |  |  | NPS have not yet issued a CSO condition under TDC project
Anglian Water | HOLLAND-HAVEN (NEW P S) TPS | ASENF2386A | CSO | N/a | Holland |  |  |  | NPS have not yet issued a CSO condition under TDC project
Anglian Water | Holme next the sea - BEECH RD SPS | AW4NF193X/V001 | EO | North East Wash | N/a | 158.3 | 15 | 100%
Anglian Water | HOLT-MAIN ROAD STW | AW4NF118AW/V001 | CSO | N/a | N/a | 17.25 | 2 | 100%
Anglian Water | HORHAM TPS | ASENF3039/12060/V001 | CSO | N/a | N/a | 40 | 9 | 100%
Anglian Water | HORNCASTLE-BANOVALLUM OV | ANNNF2770/V001 | CSO | N/a | N/a | 282.5 | 28 | 94.37%
Anglian Water | HORNCASTLE-SPORTS GROUND SSO | ANNNF/1760/V001 | CSO | N/a | N/a | 3934.25 | 197 | 98.94% | SOAF investigation (Storm Overflow Assesment Framework) with EA agreement in progress
Anglian Water | HORNCASTLE-THORNTON LA TPS | AW3NF/4061/863 | CSO | N/a | N/a | 90.25 | 10 | 100%
Anglian Water | HORNING-KNACKERS WOOD STW | AW4NF521/V001 | CSO | N/a | N/a | 7960.9997 | 306 | 100% | 3rd Party flooding into catchment
Anglian Water | HULLBRIDGE-FERRY RD 2 PS | AW2NFE15768/V001 | CSO | N/a | N/a | 0 | 0 | 99.94%
Anglian Water | HULLBRIDGE-FERRY RD SP | AW2TS670/V001 | CSO | N/a | N/a | 44.5 | 7 | 100%
Anglian Water | HULLBRIDGE-WHITE POST CRNR TPS | AW2NFE18369/V001 | CSO | N/a | N/a | 120.5 | 15 | 100%
Anglian Water | HUMBERSTONE-HUMBERSTONE RD SSO | ANNNF2313/V003 | CSO | N/a | N/a | 795.25 | 63 | 91.88% | Under investigation
Anglian Water | Hunstanton - Smugglers Lane ps | ASENF12024/V001 | CSO / EO | North West Norfolk | N/a | 55.7667 | 40 | 99.97%
Anglian Water | Hunstanton Storm Overflow 1 (HUNSTANTON SOUTH END ROAD TPS) | AECCS660/10416/V001 | CSO | N/a | Hunstanton Main Beach | 21.9667 | 22 | 100%
Anglian Water | HUNTINGDON (GODMANCHESTER) STW | AWCNF/1106/B269/V004 | CSO | N/a | N/a | 171.5 | 12 | 100%
Anglian Water | Huntingdon Hartford Rd SP | AWCNF/11842/V001 | CSO | N/a | N/a | 146.0333 | 61 | 100% | Proposed SOAF investigation (Storm Overflow Assesment Framework) with EA agreement
Anglian Water | IMMINGHAM SEA OUTFALL | ANNTS3940/13654/V001 | CSO | N/a | N/a | 398 | 136 | 99.99% | Possible SOAF investigation (Storm Overflow Assesment Framework) with EA agreement
Anglian Water | INGOLDISTHORPE-SANDY LANE TPS | AECNF719/11043/V001 | CSO | N/a | N/a | 27.75 | 8 | 100%
Anglian Water | INGOLDISTHORPE STW | AECNF1108/V001 | CSO | N/a | N/a | 474.75 | 31 | 100%
Anglian Water | Ingoldmells - Southgate Camp | ANNNF2604/AW3NFF1185 | CSO | N/a | Ingoldsmells South |  |  |  | NPS have not yet issued a CSO condition under TDC project
Anglian Water | INGOLDMELLS STW | ANNCS3740/13577/V003 | CSO | N/a | N/a | 7 | 10 | 99.97%
Anglian Water | Ingoldmells (STW) PS | ANNTS3539/13470/V001 | CSO | N/a | Ingoldsmell South | 13.0667 | 6 | 100%
Anglian Water | IPSWICH-CLIFF QUAY RAEBURN ST | AEETS/3234/12128/V001 | CSO | N/a | N/a | 504 | 89 | 100% | Operational issue resolved, under further investigation
Anglian Water | Ipswich - Dock Street PS | AW4TS1430/12087/V001 | CSO | N/a | N/a | 30.2 | 19 | 99.85%
Anglian Water | Ipswich - Portmans Walk tank | ASETS3273/12153/V001 | CSO | N/a | N/a | 5.1 | 6 | 98.9%
Anglian Water | Ipswich - Stoke Bridge CSO | ASETS3275/12155/V001 | CSO | N/a | N/a | 8.5 | 6 | 100%
Anglian Water | IPSWICH-WHERSTEAD RD SP | AW4TS/1431/V001 | CSO | N/a | N/a | 18.75 | 20 | 100%
Anglian Water | Ipswich - Wolsey Street PS | AW4TS1427/12083 | CSO | N/a | N/a | 2.9667 | 22 | 66.17% | Under investigation
Anglian Water | IPSWICH-YARMOUTH RD BF | ASETS3277 | CSO | N/a | N/a | 2 | 3 | 97.01%
Anglian Water | IRCHESTER TPS | AWNNF2403A | CSO | N/a | N/a |  |  |  | NPS have not yet issued a CSO condition under TDC project
Anglian Water | IRTHLINGBOROUGH-CROUCH RD SSO | EPR/NB3691NS/V001 | CSO | N/a | N/a | 10.75 | 18 | 99.23%
Anglian Water | IRTHLINGBOROUGH SP | AWNNF2404/V003 | CSO | N/a | N/a | 1.5 | 1 | 100%
Anglian Water | ISLIP STW | AW5NF/557/V002 | CSO | N/a | N/a | 764 | 38 | 100%
Anglian Water | Jaywick - Brooklands Gardens PS | ASENF3334/12238/V001 | CSO | N/a | Jaywick | 0.033333 | 1 | 99.98%
Anglian Water | JAYWICK NEW STW | AEECS12400/V002 | CSO | N/a | N/a | 299.25 | 88 | 99.53% | Possible SOAF investigation (Storm Overflow Assesment Framework) with EA agreement
Anglian Water | KEMPSTON-VILLAGE HALL PS | AW1NF1320/V002 | CSO | N/a | N/a | 0.25 | 1 | 89.07% | Under investigation
Anglian Water | KESSINGLAND-MARSH LN STW | AW4NF/358X/V001 | CSO | N/a | N/a | 300.75 | 24 | 99.92%
Anglian Water | KINGS LYNN AUSTIN STREET OV | AECTS543/7 | CSO | N/a | N/a | 11.5 | 13 | 100%
Anglian Water | KINGS LYNN BLACKFRIARS RD OV | AECTS543/6 | CSO | N/a | N/a | 11.5 | 13 | 100%
Anglian Water | KINGS LYNN BLACKFRIARS ST OV | AECTS543/5 | CSO | N/a | N/a | 11.5 | 13 | 100%
Anglian Water | KINGS LYNN EXTONS RD OV | AECTS543/3 | CSO | N/a | N/a | 11.5 | 13 | 100%
Anglian Water | KINGS LYNN FERRY STREET OV | AECTS477/10312/V002 | CSO | N/a | N/a | 3 | 7 | 93.49%
Anglian Water | KINGS LYNN-FRIARS OV | AW1NF914/V001 | CSO | N/a | N/a | 1 | 3 | 95.47%
Anglian Water | Kings Lynn - Gaywood Outfall | AECTS433/11056/V001 | CSO | South East Wash | N/a | 275.4333 | 53 | 100%
Anglian Water | KINGS LYNN-GAYWOOD OUTFALL 2 OV | AECTS439/11057/V001 | CSO | N/a | N/a | 275.75 | 52 | 100%
Anglian Water | KINGS LYNN GAYWOOD ROAD OV | AECTS543/14 | CSO | N/a | N/a | 11.5 | 13 | 100%
Anglian Water | KINGS LYNN GOODWINS ROAD OV | AECTS543/2 | CSO | N/a | N/a | 11.5 | 13 | 100%
Anglian Water | KINGS LYNN-HIGHGATE OV | AECNF740/11032/V001 | CSO | N/a | N/a | 29.25 | 13 | 100%
Anglian Water | KINGS LYNN KING GEORGE V AV OV | AECTS543/11 | CSO | N/a | N/a | 11.5 | 13 | 100%
Anglian Water | KINGS LYNN LOKE ROAD EAST OV | AECTS543/15 | CSO | N/a | N/a | 11.5 | 13 | 100%
Anglian Water | KINGS LYNN-MILLFLEET SO1 OV | AW1NF1040/V001 | CSO | N/a | N/a | 79.25 | 71 | 99.45% | Under investigation
Anglian Water | KINGS LYNN-MILLFLEET SO2 OV | AW1NF1041/V001 | CSO | N/a | N/a | 394.75 | 71 | 35.73% | SOAF investigation (Storm Overflow Assesment Framework) with EA agreement in progress
Anglian Water | KINGS LYNN-MILLFLEET SO3 OV | AW1NF1042/V001 | CSO | N/a | N/a | 2.25 | 4 | 65.1% | Operational issue being resolved, under further investigation
Anglian Water | KINGS LYNN-NAR LANE SP | AECTS543/10364 | CSO | N/a | N/a | 11.5 | 13 | 100%
Anglian Water | KINGS LYNN PAGESTAIR LANE OV | EPR/NB3292AG/V001 | CSO | N/a | N/a | 0 | 0 | 99.88%
Anglian Water | Kings Lynn - Purfleet Quay PS | AECTS677/10467/V002 | CSO / EO | South East Wash | N/a | 54.6333 | 32 | 100%
Anglian Water | KINGS LYNN STW | AECTS3037/11334/V001 | CSO | N/a | N/a | 11.5 | 3 | 100%
Anglian Water | KINGS LYNN TENNYSON AV (N) OV | AECTS543/12 | CSO | N/a | N/a | 11.5 | 13 | 100%
Anglian Water | KINGS LYNN TENNYSON AV (S) OV | AECTS543/10 | CSO | N/a | N/a | 11.5 | 13 | 100%
Anglian Water | KINGS LYNN TENNYSON RD OV | AECTS543/4 | CSO | N/a | N/a | 11.5 | 13 | 100%
Anglian Water | KINGS LYNN TUESDAY MKT PL OV | EPR/NB3291NA/V001 | CSO | N/a | N/a | 0.75 | 3 | 100%
Anglian Water | KINGS LYNN WATER LANE OV | EPR/NB3291WL/V001 | CSO | N/a | N/a | 3.25 | 8 | 100%
Anglian Water | KINGS LYNN WOOTTON QE AV OV | AECTS543/18 | CSO | N/a | N/a | 11.5 | 13 | 100%
Anglian Water | KINGS LYNN WOOTTON RIVER LN OV | AECTS543/16 | CSO | N/a | N/a | 11.5 | 13 | 100%
Anglian Water | Kirby Main Maltings sp | ASENF3692/12395/V001 | CSO / EO | Walton Backwaters | N/a | 169.3 | 59 | 100%
Anglian Water | KIRTON-DRUNKARDS L STW | ASENF/938/12042/V001 | CSO | Deben | N/a | 16.9 | 2 | 100%
Anglian Water | KISLINGBURY SP | AWNNF13462/V001 | CSO | N/a | N/a | 25 | 16 | 90.37%
Anglian Water | LACEBY-CAISTOR ROAD #1 SSO | ANNNF2284/V001 | CSO | N/a | N/a | 105 | 49 | 99.47% | Proposed SOAF investigation (Storm Overflow Assesment Framework) with EA agreement
Anglian Water | LATCHINGDON STW | AW2NF/E17367/V001 | CSO | N/a | N/a | 964.75 | 94 | 98.09% | SOAF investigation (Storm Overflow Assesment Framework) with EA agreement in progress
Anglian Water | LAVENDON STW | AW1NF1012/V001 | CSO | N/a | N/a | 642.75 | 70 | 99.97% | Under investigation
Anglian Water | LEIGHTON BUZD-CHAINBRIDGE SP | AWCNF/11872/V001 | CSO | N/a | N/a | 79.25 | 6 | 100%
Anglian Water | LEIGHTON LINSLADE STW | AWCNF608/10415/V004 | CSO | N/a | N/a | 836.5 | 54 | 100%
Anglian Water | LEISTON-MAIN ST(1) | EPR/NB3694RC/V001 | CSO | N/a | N/a | 0.25 | 1 | 99.99%
Anglian Water | LEISTON-MAIN ST(2) | EPR/NB3694VV/V001 | CSO | N/a | N/a | 0.5 | 2 | 100%
Anglian Water | LEISTON-MAIN STREET(3) | EPR/NB3695AY/V001 | CSO | N/a | N/a | 2.5 | 6 | 99.99%
Anglian Water | LEISTON-VALLEY RD STW | ASENF1122/V002 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | LEISTON-VALLEY ROAD/CROWN STREET | EPR/NB3695EB/V001 | CSO | N/a | N/a | 1.75 | 4 | 99.99%
Anglian Water | LEISTON-VALLEY ROAD/CROWN STREET(2) | EPR/NB3695RN/V001 | CSO | N/a | N/a | 74 | 59 | 99.99% | Proposed SOAF investigation (Storm Overflow Assesment Framework) with EA agreement
Anglian Water | LEISTON-WATERLOO AVENUE (1) | EPR/NB3695WR/V001 | CSO | N/a | N/a | 4 | 14 | 99.99%
Anglian Water | LEISTON-WATERLOOAVENUE/PARK HILL (1) | EPR/NB3696NC/V001 | CSO | N/a | N/a | 27 | 38 | 99.99%
Anglian Water | LEISTON-WATERLOO AVENUE/PARK HILL(2) | EPR/NB3696AQ/V001 | CSO | N/a | N/a | 3 | 9 | 99.95%
Anglian Water | LEISTON - WATERLOO PARK(2) | EPR/NB3694EQ/V001 | CSO | N/a | N/a | 14 | 24 | 100%
Anglian Water | LETCHWORTH-NORTON COMMON SSO | AW1NF805/V001 | CSO | N/a | N/a | 10.5 | 11 | 99.83%
Anglian Water | LETCHWORTH STW | AWCNF1123v003 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | Lincoln - Brayford way SP | ANNNF3278/13386/V001 | CSO | N/a | N/a | 9.0667 | 8 | 100%
Anglian Water | LINTON STW | ASCNF/1125/V001 | CSO | N/a | N/a | 26.5 | 7 | 99.12%
Anglian Water | LITTLEPORT-FRIARS WY WIS RD | AECNF3106/11357/V001 | CSO | N/a | N/a | 2 | 6 | 100%
Anglian Water | LITTLEPORT-HOOF CLOSE SSO | AECNF3123/11305/V001 | CSO | N/a | N/a | 58.75 | 60 | 99.99%
Anglian Water | LITTLEPORT, PONT'S HILL | EPR/PB3392RM/V001 | CSO | N/a | N/a | 45.5 | 17 | 99.99%
Anglian Water | LITTLEPORT-WISBECH ROAD TPS | EPR/PB3392NP/V001 | CSO | N/a | N/a | 59 | 16 | 94.99%
Anglian Water | LODDON-KNAPPS BRIDGE SP | EPR/DP3728GJ/V004 | CSO | N/a | N/a | 14.75 | 6 | 100%
Anglian Water | LOUTH-BRACKENBOROUGH RD SSO | ANNNF3594/13592/V002 | CSO | N/a | N/a | 1 | 3 | 99.01%
Anglian Water | LOUTH-BRIDGE ST SSO | ANNNF3593/13591/V002 | CSO | N/a | N/a | 44.5 | 43 | 97.62%
Anglian Water | LOUTH-BROADBANK SSO | ANNNF3587/13585/V002 | CSO | N/a | N/a | 560.25 | 64 | 98.57% | Under investigation
Anglian Water | LOUTH-CHURCH LIGHTS SSO | ANNNF/3592/13590/V002 | CSO | N/a | N/a | 49.25 | 49 | 99.91%
Anglian Water | LOUTH-GRAYS ROAD SSO | ANNNF3583/13583/V002 | CSO | N/a | N/a | 110.25 | 51 | 92.17%
Anglian Water | LOUTH-GRIMSBY RD CISTERN SSO | ANNNF3588/13586/V002 | CSO | N/a | N/a | 3 | 7 | 97.3%
Anglian Water | LOUTH-JAMES ST SSO | ANNNF3590/13588/V002 | CSO | N/a | N/a | 16.75 | 35 | 94.75%
Anglian Water | LOUTH-KENWICK ROAD SSO | ANNNF/1763/V001 | CSO | N/a | N/a | 3.75 | 6 | 89.66% | Under investigation
Anglian Water | LOUTH-NEWBRIDGE HILL SSO | ANNNF3591/13589/V002 | CSO | N/a | N/a | 10.5 | 15 | 98.5%
Anglian Water | LOUTH RAMSGATE ROAD MH749A FDT | EPR/GB3790RQ | CSO | N/a | N/a | 1.5 | 6 | 86.22% | Under investigation
Anglian Water | LOUTH-RAMSGATE SSO | ANNNF3585/13584/V002 | CSO | N/a | N/a | 14.5 | 30 | 99.96%
Anglian Water | LOUTH SPAW LANE SSO | ANNNF3589v002 | CSO | N/a | N/a | 1446.75 | 136 | 99.83% | SOAF investigation (Storm Overflow Assesment Framework) with EA agreement in progress
Anglian Water | LOUTH STW | ANNNF1131/V001 | CSO | N/a | N/a | 103.5 | 32 | 99.97%
Anglian Water | Lowestoft - Belvedere Road Overflow | ASETS16995/V001 | CSO | N/a | Lowestoft North | 8.9 | 11 | 99.99%
Anglian Water | Lowestoft - Boulevard PS & CSO (AKA Oulton Broad-Holly RD TPS) | AW4TS1419/12088/V001 | CSO | N/a | N/a | 2.3333 | 18 | 99.86%
Anglian Water | Lowestoft - Bridge PS | ASETS2159A | CSO | N/a | Lowestoft North |  |  |  | NPS have not yet issued a CSO condition under TDC project
Anglian Water | LOWESTOFT COMMERICAL RD | ASETS4083/16994/V002 | CSO | N/a | N/a | 125.2333 | 22 | 25.57% | Under investigation
Anglian Water | Lowestoft - Marina CSO | ASETS4083/16991/V001 | CSO | N/a | Lowestoft North | 105.0333 | 83 | 99.92% | Catchment investigation underway
Anglian Water | LOWESTOFT-ROTTERDAM RD #1 SO | EPR/LB3996NV/V001 | CSO | N/a | N/a | 35.2667 | 43 | 96.52%
Anglian Water | Lowestoft - Royal Norfolk & Suffolk Yacht Club (Lowestoft Harbour Bridge SP) | AW4TS12090/V001 | CSO | N/a | Lowestoft North | 200.5667 | 109 | 99.84% | Catchment investigation underway
Anglian Water | Lowestoft - Station Square #1 CSO | ASETS4083/16993/V001 | CSO | N/a | Lowestoft North | 27.9333 | 27 | 95.93%
Anglian Water | Lowestoft - Station Square #2 & Commercial Rd CSO | EPR/JB3496WZ/V001 | CSO | N/a | Lowestoft North | 14.8 | 26 | 99.17%
Anglian Water | Lowestoft - St John's Road CSO | ASETS4082/16950/V001 | CSO | N/a | Lowestoft North | 60.8667 | 117 | 100% | Catchment investigation underway
Anglian Water | LOWESTOFT-ST PETER'S ST/YEOVIL RD | EPR/MB3495DR/V001 | CSO | N/a | N/a | 0.5 | 2 | 99.9%
Anglian Water | LUDHAM-WOMACK STAITHE TPS | AEENF/91910/10202/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | Mablethorpe - George St CSO | ANNNF/892/V001 | CSO | N/a | Mablethorpe Town | 6.8 | 11 | 99.95%
Anglian Water | MABLETHORPE STW | ANNNF3078/13149/V001 | CSO | N/a | N/a | 186.5 | 24 | 100%
Anglian Water | MABLETHORPE STW | ANNNF3078/13149/V001_ST10 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | MABLETHORPE STW | ANNNF3078/13149/V001_ST9 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | Maidenhall Storm outfall | AW4TS1429/V001 | CSO | N/a | N/a | 16.3 | 17 | 100%
Anglian Water | Maldon - Park Drive | AW2NFE03278/V001 | CSO | N/a | N/a | 141.9333 | 23 | 96.51%
Anglian Water | Maldon STW | ASENF1136/V001 | CSO | Osea Island | N/a | 1488.1667 | 86 | 100% | Proposed SOAF investigation (Storm Overflow Assesment Framework) with EA agreement
Anglian Water | MANTHORPE-MILL SP | ANNNF851/13024/V002_Outlet 1 | CSO | N/a | N/a | 97.75 | 8 | 100%
Anglian Water | MARCH-CREEK RD/ST JOHNS RD OV | AECNF3511/11501/V001 | CSO | N/a | N/a | 98.5 | 21 | 97.34%
Anglian Water | MARCH-DARTFORD/ELLIOTT RD OV | AECNF3512/11502/V001 | CSO | N/a | N/a | 73 | 18 | 99.82%
Anglian Water | MARCH-ELLIOT RD OV | AW1NF3189/V001 | CSO | N/a | N/a | 37.5 | 6 | 99.71%
Anglian Water | MARCH-ELWYN RD/EL CT OV | AECNF3513/11503/V001 | CSO | N/a | N/a | 80.5 | 18 | 99.98%
Anglian Water | MARCH-WINDSOR DRIVE OV | AECNF3514/11568/V001 | CSO | N/a | N/a | 627.5 | 50 | 99.14%
Anglian Water | MARKET HARBOROUGH-RIVERSIDESSO | AW5NF1798/V001 | CSO | N/a | N/a | 297.25 | 18 | 100%
Anglian Water | MARKET RASEN-CAISTOR ROAD OV | ANNNF3266/13383/V001 | CSO | N/a | N/a | 12 | 11 | 92.99%
Anglian Water | MARTLESHAM M BRIDGE SP | ASENF2160/V002 | CSO / EO | Deben | N/a | 0 | 0 | 99.2%
Anglian Water | MAYLANDSEA STW | ASETS/10531/V001 | CSO | N/a | N/a | 472.5 | 50 | 77.74% | Changed to alternative monitor type, now resolved
Anglian Water | MELBOURN STW | AW1NF934/V001 | CSO | N/a | N/a | 92.75 | 62 | 100% | Operational issue being resolved, under further investigation
Anglian Water | MELTON CONSTABLE-BURGH BECK SP | AEENF3883/12431/V001 | CSO | N/a | N/a | 28.25 | 5 | 100%
Anglian Water | MILDENHALL STW | ASCNF11025/V003 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | MUNDESLEY-KNAPTON RD OUTFALL | AEECS3731/12411/V001 | CSO | N/a | N/a | 64 | 23 | 100%
Anglian Water | Mundesley - The Dell Chalet Park | AEENF791/10515/V001 | CSO | N/a | Mundesley | 3.3 | 14 | 99.99%
Anglian Water | MUNDESLEY-THE PROMENADE SP | AEECS3350/12196/V001 | CSO | N/a | Mundesley | 3.8 | 2 | 91.79%
Anglian Water | MUNDFORD STW | AECNF/2080/V002 | CSO | N/a | N/a | 298.5 | 39 | 99.57%
Anglian Water | NASSINGTON STW | AW5NF141/V001 | CSO | N/a | N/a | 0 | 0 | 57.67% | Changed to alternative monitor type, now resolved
Anglian Water | NASSINGTON TPS | AWNNF3725/13572/V001 | CSO | N/a | N/a | 110.25 | 13 | 100%
Anglian Water | NEWNHAM STW (NORTHANTS) | AW5NF/400/V002 | CSO | N/a | N/a | 2859.75 | 149 | 100% | SOAF investigation (Storm Overflow Assesment Framework) with EA agreement in progress
Anglian Water | NEWPORT PAGNELL-WILLEN RD TPS | AW1NF3235/V001 | CSO | N/a | N/a | 7.75 | 1 | 100%
Anglian Water | NEWTON FLOTMAN-MAIDS HEAD TPS | AEENF796/12009/V001 | CSO | N/a | N/a | 70.5 | 20 | 100%
Anglian Water | NEWTON LONGVILLE-WHADDON RD SP | AWCNF3755/1310/V001 | CSO | N/a | N/a | 215 | 40 | 100%
Anglian Water | NORMANBY-PARK SP | ANNNF3482/13442/V001 | CSO | N/a | N/a | 11.75 | 6 | 100%
Anglian Water | NORTHAMPTON ABINGTON TANK SSO | AWNNF3566/13522/V002 | CSO | N/a | N/a | 20.8 | 5 | 99.99%
Anglian Water | Northampton - Becketts Park SSO | AW5NF1832/V001 | CSO | N/a | N/a | 57.9333 | 42 | 100%
Anglian Water | Northampton Bedford Rd PS (storm & EO) | AW5NF1778/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | NORTHAMPTON-BEDFORD ROAD SSO | EPR/JB3297WF/V001a | CSO | N/a | N/a | 4.4 | 12 | 100%
Anglian Water | NORTHAMPTON-BRIDGE ST OV | EPR/JB3297NS/V001 | CSO | N/a | N/a | 36.9 | 39 | 100%
Anglian Water | NORTHAMPTON-DUSTON SYCAMORESSO | AW5NF384/V002 | CSO | N/a | N/a | 130.8 | 111 | 100% | SOAF investigation (Storm Overflow Assesment Framework) with EA agreement in progress
4463.173327 | NORTHAMPTON-LOWER HESTER ST OV | EPR/JB3297AZ/V001 | CSO | N/a | N/a | 18.3667 | 14 | 99.98%
Anglian Water | NORTHAMPTON-MALCOLM DRIVE SSO | AW5NF352/V001 | CSO | N/a | N/a | 44.5 | 13 | 99.92%
Anglian Water | NORTHAMPTON-MH 15, DUSTON | EPR/JB3296RM/V001 | CSO | N/a | N/a | 0.96667 | 8 | 99.99%
Anglian Water | NORTHAMPTON-MILL LANE SSO | EPR/JB3297EW/V001 | CSO | N/a | N/a | 0.033333 | 1 | 100%
Anglian Water | NORTHAMPTON-SPENCER BRIDGE R | EPR/JB3296WT/V001 | CSO | N/a | N/a | 69.6 | 46 | 100%
Anglian Water | NORTHAMPTON-SWAN ST SSO | EPRJB3297VH/V001 | CSO | N/a | N/a | 0.8 | 6 | 100%
Anglian Water | NORTHAMPTON-VICTORIA GARDENS | EPR/JB3297RX/V001 | CSO | N/a | N/a | 5.8333 | 33 | 100%
Anglian Water | NORTH COTES STW | ANNNF1298/V001 | CSO | N/a | N/a | 17 | 7 | 100%
Anglian Water | NORTHILL-ICKWELL ROAD SP | AW1NF368/V001 | CSO | N/a | N/a | 270.75 | 25 | 100%
Anglian Water | NORTH THORESBY STW | ANNNF180/10292/V001 | CSO | N/a | N/a | 64.5 | 12 | 100%
Anglian Water | NORTH WALSHAM-BLUEBELL RD OV | AEENF3132/12104/V001 | CSO | N/a | N/a | 8 | 4 | 100%
Anglian Water | NORWICH ANGEL ROAD MM MH7301 | EPR/EB3297AK | CSO | N/a | N/a | 0 | 0 | 0% | Under investigation
Anglian Water | NORWICH-BARRACK STREET SSO | EPR/MB3699EK/V001 | CSO | N/a | N/a | 1 | 4 | 100%
Anglian Water | NORWICH - BISHOPBRIDGE ROAD | EPR/NB3591EE/V001 | CSO | N/a | N/a | 5710.25 | 248 | 100% | Catchment investigation underway
Anglian Water | NORWICH, BRACONDALE CSO | EPR/HB3693DN/V001 | CSO | N/a | N/a | 159 | 18 | 100%
Anglian Water | NORWICH CARROW ROAD MM MH2811 | EPR/EB3296AX | CSO | N/a | N/a | 49.4667 | 43 | 100%
Anglian Water | NORWICH CEDAR ROAD MM MH4010 | EPR/EB3296EH | CSO | N/a | N/a | 16.5333 | 33 | 94.34%
Anglian Water | NORWICH - CHALK HILL RD | EPR/NB3591RM/V001 | CSO | N/a | N/a | 884.75 | 44 | 100%
Anglian Water | Norwich - Cow Tower CSO | AEETF 3260/12149/V001 | CSO | N/a | N/a | 13.6333 | 10 | 99.98%
Anglian Water | NORWICH-ELM HILL SSO | EPR/MB3699DG/V001 | CSO | N/a | N/a | 4081 | 172 | 100% | Changed to alternative monitor type, now resolved
Anglian Water | NORWICH FAITHS LANE MM MH5703 | EPR/GB3293VQ | CSO | N/a | N/a | 85.4 | 31 | 35.04% | Operational issue now resolved
Anglian Water | NORWICH-GIBRALTAR GARDENS CSO | AEENF3467/12369/V001 | CSO | N/a | N/a | 316.25 | 34 | 90.08%
Anglian Water | NORWICH - KETTS HILL | EPR/NB3591AF/V001 | CSO | N/a | N/a | 4.25 | 7 | 99.9%
Anglian Water | NORWICH-KING STREET SSO #2 | EPR/MB3699WS/V001 | CSO | N/a | N/a | 22.75 | 15 | 99.87%
Anglian Water | Norwich Lower Close (Ferry Lane) | EPR/GB3293WP | CSO | N/a | N/a | 0.66667 | 3 | 99.77%
Anglian Water | NORWICH-NEW MILLS SSO | EPR/MB3699AM/V001 | CSO | N/a | N/a | 0.5 | 2 | 99.86%
Anglian Water | NORWICH-PEACOCK STREET SSO | EPR/MB3699RY/V001 | CSO | N/a | N/a | 3697 | 156 | 100% | Catchment investigation underway
Anglian Water | NORWICH-PRINCE OF WALES ROAD MH5501 FDT | EPR/GB3598AA | CSO | N/a | N/a | 32.8333 | 33 | 98.14%
Anglian Water | NORWICH - RIVER LANE | EPR/NB3590WG/V001 | CSO | N/a | N/a | 0.5 | 2 | 97.46%
Anglian Water | NORWICH RIVERSIDE ROAD MM MH0902 | EPR/EB3296RQ | CSO | N/a | N/a | 1241.4333 | 256 | 100% | Catchment investigation underway
Anglian Water | NORWICH - ROSARY ROAD | EPR/NB3591NP/V001 | CSO | N/a | N/a | 0 | 0 | 99.94%
Anglian Water | NORWICH SANDY LANE MM MH1902 | EPR/EB3296WM | CSO | N/a | N/a | 4103.1333 | 224 | 76.75% | Catchment investigation underway
Anglian Water | Norwich, School Lane/Bedford Street | EPR/EB3296NR | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | NORWICH - TURNING BASIN | AW4TF777X/V003 | CSO | N/a | N/a | 91.5 | 56 | 99.96%
Anglian Water | OAKHAM STW | AW5NF/5211/V003_CSO | CSO | N/a | N/a | 391.5 | 71 | 99.99% | SOAF investigation (Storm Overflow Assesment Framework) with EA agreement in progress
Anglian Water | OAKHAM STW | AW5NF/5211/V003_SSO | CSO | N/a | N/a | 0 | 0 | 100% | SOAF investigation (Storm Overflow Assesment Framework) with EA agreement in progress
Anglian Water | ODELL STW | AW1NF1081/V003 | CSO | N/a | N/a | 4193.25 | 185 | 100% | Under investigation
Anglian Water | Oundle - Barnwell Rd TPS | AWNNF2127/V002 | CSO | N/a | N/a | 21.5333 | 7 | 100%
Anglian Water | Oundle - East Rd CSO | EPR/LB3592AF/V001 | CSO | N/a | N/a | 2.4 | 13 | 100%
Anglian Water | Oundle - New Rd TPS | AWNNF2492/V001 | CSO | N/a | N/a | 51.1333 | 15 | 100%
Anglian Water | Oundle STW SSO | AW5NF809/V002 | CSO | N/a | N/a | 423.6333 | 53 | 100%
Anglian Water | PAGLESHAM-CHURCH END SP | ASENF454/10351/V001 | CSO | N/a | N/a | 82.75 | 16 | 100%
Anglian Water | Paglesham East TPS | ASENF2520A | CSO / EO | Upper Roach | N/a |  |  |  | NPS have not yet issued a CSO condition under TDC project
Anglian Water | PAGLESHAM-WEST TPS | ASENF455/10352/V001 | CSO | N/a | N/a | 107.75 | 12 | 100%
Anglian Water | Peldon - SPS at Mersea Road AKA PELDON-ROSE COTTAGE SP | AW2NFE05472/V001 | EO | Strood Channel | N/a | 9.3 | 12 | 98.79%
Anglian Water | PETBORO-ORTON MERE SP | AW5NF567/V001 | CSO | N/a | N/a | 27.5 | 3 | 100%
Anglian Water | PETBORO-WERRTON LINCOLN RD SSO | AW5NF1818/V001 | CSO | N/a | N/a | 13.75 | 4 | 100%
Anglian Water | PETERBOROUGH (FLAG FEN) STW | AW5NF5178_3DWF | CSO | N/a | N/a | 1135.75 | 127 | 100% | Scheme in place to address high flows
Anglian Water | PETERBOROUGH (FLAG FEN) STW | AW5NF5178_6DWF | CSO | N/a | N/a | 1492 | 87 | 100% | Scheme in place to address high flows
Anglian Water | Peterborough - North Minster (PETERBOROUGH-NEW RD/ST J RD CS) | AW/5/NF/620/V001 | CSO | N/a | N/a | 16.4 | 4 | 100%
Anglian Water | Peterborough - Oundle Rd SSO | AW5NF/1793/V001 | CSO | N/a | N/a | 245.2 | 34 | 100%
Anglian Water | Peterborough - River Lane SSO | AW5NF/1794/V001 | CSO | N/a | N/a | 13.3333 | 28 | 99.76%
Anglian Water | PIRTON TPS | AWENF2531/V002 | CSO | N/a | N/a | 94 | 23 | 100%
Anglian Water | PIRTON TPS | EPR/RB3894EG | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | PITSEA STW | CSSC.4457/V001 | CSO | N/a | N/a | 66.5 | 28 | 100%
Anglian Water | POPPYHILL STW | AW1NF2418/V003 | CSO | N/a | N/a | 198.5 | 18 | 100%
Anglian Water | Prittle Brook Storage Tank | S/WR76/V001 | CSO | Foulness | N/a | 6.4 | 4 | 99.86%
Anglian Water | Promenade Sewer Storage Tank, Overstrand, Norfolk | AEECS990/12053/V001 | CSO | N/a | N/a | 34.75 | 16 | 99.99%
Anglian Water | Ramsey Island - St Lawrence Drive PS | ASENF/3982/16188/V001 | CSO / EO | Osea Island/Blackwater | N/a | 0.1 | 3 | 100%
Anglian Water | Rochford - Depot sp (storm tanks) | AW2NFE15272/V002 | CSO | Upper Roach | n/a | 7.9 | 9 | 99.73%
Anglian Water | Rochford - Depot sp (storm tanks) | AW2NFE15272/V002 | EO | Upper Roach | N/a | 39.7 | 8 | 100%
Anglian Water | Rowhedge - High Street PS | AW2NFE06884v001 | CSO / EO | Colne | N/a | 0.033333 | 1 | 100%
Anglian Water | SAFFRON WALDEN STW | ASCNF1184v001 | CSO | N/a | N/a | 7.75 | 5 | 100%
Anglian Water | SAFFRON WALDEN-VICTORIA THX OV | EPR/NB3691VH | CSO | N/a | N/a | 1 | 3 | 98.3%
Anglian Water | SANDY-GIRTFORD SSO | AWCNF1630/V003 | CSO | N/a | N/a | 28 | 25 | 99.9%
Anglian Water | SANDY-HIGH STREET SSO | AWCNF1684/V003 | CSO | N/a | N/a | 11.75 | 29 | 100% | Proposed SOAF investigation (Storm Overflow Assesment Framework) with EA agreement
Anglian Water | SAXILBY-HIGH ST/MANOR RD SSO | AW3NF838/V001 | CSO | N/a | N/a | 31.25 | 16 | 99.99%
Anglian Water | SAXILBY-HIGH ST/WEST BANK SSO | AW3NF837/V001 | CSO | N/a | N/a | 2 | 1 | 99.96%
Anglian Water | S BENFLEET-HALL FARM RD SP | EPR/NB3199DJ/V001 | CSO | N/a | N/a | 42 | 38 | 100%
Anglian Water | SCAWBY SEWER SSO | AW3NFF795/V001 | CSO | N/a | N/a | 1.25 | 3 | 100%
Anglian Water | Sea Palling - Clink Road SPS | AW4NF894X/V001 | CSO | N/a | Sea Palling | 51.9333 | 14 | 100%
Anglian Water | Sea Palling - Waxham Road SPS | AW4NF895X/V001 | CSO | N/a | Sea Palling | 52.2667 | 6 | 100%
Anglian Water | Sheringham East Beach Sewage Tank (AKA SHERINGHAM BEACH RD TPS) | AEECS867/12070/V001 | CSO | N/a | Sherringham | 4.3 | 4 | 99.99%
Anglian Water | SIBLE HEDINGHAM-ALDERFORD ST | AW2NFE36066/V002 | CSO | N/a | N/a | 24.75 | 11 | 96.65%
Anglian Water | SILVERSTONE STW | AWCNF1191/V002 | CSO | N/a | N/a | 1760.25 | 94 | 100% | SOAF investigation (Storm Overflow Assesment Framework) with EA agreement in progress
Anglian Water | SKELLINGTHORPE, LINCOLN RD CSO | ANNNF3543/13437/V001 | CSO | N/a | N/a | 4 | 2 | 100%
Anglian Water | SOHAM-CHERRY TREE SP | AECNF3534/11498/V005 | CSO | N/a | N/a | 9.25 | 2 | 96.34%
Anglian Water | SOHAM STW | AECNF1195v004 | CSO | N/a | N/a | 467.25 | 34 | 100%
Anglian Water | Southend - Burdett Rd CSO | S/WR86/V001 | CSO | Foulness | N/a | 5.4333 | 6 | 99.98%
Anglian Water | SOUTHEND-EASTWOOD PK SOUTH SSO | AW2NFE/03958/V001 | CSO | N/a | N/a | 0.5 | 2 | 66.1% | Under investigation
Anglian Water | SOUTHEND-LEIGH BF CSO (AKA Southend Belton Gardens PS TK OV) | S/WR73/V001 | CSO | N/a | N/a | 36.5 | 6 | 99.94%
Anglian Water | Southend - Manilla Rd | S/WR87/V001 | CSO | Foulness | N/a | 55 | 11 | 99.98%
Anglian Water | SOUTHEND-PRIORY CRESCENT SSO | AW2NFE05183/V001 | CSO | N/a | N/a | 1 | 1 | 99.81%
Anglian Water | SOUTHEND-ROCHFORD RD SSO | AW2NFE05483/V001 | CSO | N/a | N/a | 14.75 | 6 | 99.98%
Anglian Water | Southend - Towerfield INT SP | AW2NFE12684/V001 | EO | Foulness | N/a | 13.4 | 6 | 100%
Anglian Water | SOUTHEND-VICTORIA AVE SSO (Southend - Bell PH_Prince Avenue - SOPNFT) | AW2NFE17964/V001 | CSO | N/a | N/a | 31 | 12 | 98.86%
Anglian Water | SOUTHEND-VICTORIA W'F TANK CSO | S/WR74/V001 | CSO | N/a | N/a | 0.25 | 1 | 99.55%
Anglian Water | Southwold - Gardener Road PS | ASENF91767/10176/V001 | CSO | N/a | Southwold the Deans | 7.2333 | 36 | 98.35%
Anglian Water | Southwold - Marlborough Rd SSO | AW4NF1768v001 | CSO | N/a | Southwold the Pier | 0.26667 | 7 | 99.96%
Anglian Water | Southwold - South Green SPS (southwold - ferry rd) | AW4TS757X/V001 | CSO | N/a | Southwold the Deans | 0.36667 | 1 | 100%
Anglian Water | Southwold - Station Rd SSO | AW4NF1762/V001 | CSO | N/a | Southwold the Pier | 4.9667 | 38 | 99.92%
Anglian Water | Southwold STW Inlet Pumping Station EO | ASETS/10380/V002/1 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | Southwold STW Settled Storm | ASETS/10380/V002/2 | CSO | N/a | N/a | 85.5667 | 14 | 98.43%
Anglian Water | SPALDING-ALBION STREET SP | AW5NF665/V001 | CSO | N/a | N/a | 0 | 0 | 99.96%
Anglian Water | STAMFORD-HUDDS MILL TPS | AW5NF1780/V001 | CSO | N/a | N/a | 4.5 | 3 | 100%
Anglian Water | STIBBINGTON STW | AW5NF315A/V001 | CSO | N/a | N/a | 768.25 | 38 | 100%
Anglian Water | St Ives - Priory Rd | AWCNF2542/V002 | CSO | N/a | N/a | 189.8667 | 49 | 100%
Anglian Water | St Ives - The Quay | AWCNF2663/V002 | CSO | N/a | N/a | 296.9333 | 21 | 100%
Anglian Water | St Ives - The Waits | AWCNF2669/V002 | CSO | N/a | N/a | 288.6667 | 26 | 100%
Anglian Water | St Neots - Market Square STO | AW1NF/2577/V001 | CSO | N/a | N/a | 37.5333 | 27 | 100%
Anglian Water | St Osyth Mill Dam PS | AW2TSE06363v001 | EO | Colne | N/a | 0 | 0 | 99.99%
Anglian Water | St Osyth - Point Clear Rd | AW2NFE01182/V001 | CSO | Colne | N/a | 18.3333 | 4 | 99.64%
Anglian Water | Sudbury - Bailey and Coates | ASENF1728/V002 | CSO | N/a | N/a | 20.9 | 24 | 100%
Anglian Water | Sudbury - Gt Eastern Rd | ASENF3753v001 | CSO | N/a | N/a | 21.5 | 13 | 100%
Anglian Water | Sudbury STW - settled storm | ASENF1314/V004 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | Sudbury STW - settled storm | ASENF1314/V004_ST2 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | Sudbury - The Croft | ASENF1729/V002 | CSO | N/a | N/a | 6.4333 | 26 | 95.66%
Anglian Water | SWAFFHAM STW | AW1NF/1077/V001 | CSO | N/a | N/a | 105.75 | 48 | 100%
Anglian Water | SWANBOURNE STW | AWCNF644/11010/V001 | CSO | N/a | N/a | 1444.25 | 86 | 100% | Under investigation
Anglian Water | SYWELL SP | AW5NF1772/V001 | CSO | N/a | N/a | 172.5 | 31 | 100%
Anglian Water | TETNEY-NEWTON MARSH STW | ANNTS13007/V001 | CSO | N/a | N/a | 34.0667 | 31 | 100%
Anglian Water | Thrapston SPS | AW5NF1570/V001 | CSO | N/a | N/a | 43.4333 | 7 | 100%
Anglian Water | Tollesbury STW SSO | ASETS1229/V002 | CSO | Tollesbury Channel | N/a | 1201.5 | 68 | 100% | Under investigation
Anglian Water | TOWCESTER STW | AW1NF63/V003 | CSO | N/a | N/a | 455 | 42 | 100% | SOAF investigation (Storm Overflow Assesment Framework) with EA agreement in progress
Anglian Water | TOWCESTER TPS | AW1NF1178/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | Trowse PS | EPR/HB3693AF/V001 | CSO | N/a | N/a | 55.8333 | 13 | 100%
Anglian Water | Walton-on-the-Naze TPS | ASECS3376/12213/V001 | CSO | N/a | Walton | 159.1667 | 62 | 97.15% | Changed to alternative monitor type, now resolved
Anglian Water | WATTON-SWAFFHAM ROAD TPS | AECNF11906/V001 | CSO | N/a | N/a | 64.5 | 26 | 100%
Anglian Water | WELLINGBOROUGH-CHESTER ROAD | AW5NF1805/V001 | CSO | N/a | N/a | 4.5 | 6 | 99.99%
Anglian Water | WELLINGBOROUGH - HATTON PARK CSO#2 | AWNNF4113/13852/V002 | CSO | N/a | N/a | 49.75 | 10 | 99.46%
Anglian Water | WELLINGBOROUGH-MARKET ST SSO (old Cattle Market- Q810OV) | AW5NF1804/V001 | CSO | N/a | N/a | 0.25 | 1 | 99.18%
Anglian Water | West Mersea STW SSO | ASETS/1320/V005 | CSO | N/a | West Mersea | 9.4 | 14 | 97.16%
Anglian Water | West Mersea - Whittaker Way SPS | AW2NFE08984/V001 | EO | Strood Channel/Blackwater | N/a | 0.16667 | 2 | 100%
Anglian Water | West Runton - Water Lane PS | AEECS12198/V001 | CSO | N/a | N/a | 70.4333 | 30 | 97.78%
Anglian Water | WHADDON STW | AWCNF11058/V002 | CSO | N/a | N/a | 2767.75 | 158 | 100% | SOAF investigation (Storm Overflow Assesment Framework) with EA agreement in progress
Anglian Water | Whitlingham STW - settled storm | AW4TF1789/V002 | CSO | N/a | N/a | 532.3667 | 52 | 100% | Proposed SOAF investigation (Storm Overflow Assesment Framework) with EA agreement
Anglian Water | WICKHAM MARKET STW | ASENF813/10537/V001 | CSO | N/a | N/a | 1066.75 | 58 | 100%
Anglian Water | WINTERINGHAM-STATION FARM SSO | ANNNF3147/13332 | CSO | N/a | N/a | 150.75 | 54 | 100% | SOAF investigation (Storm Overflow Assesment Framework) with EA agreement in progress
Anglian Water | WOLVERTON RAIL FREIGHT MD SSO | AW1NF/121/V001 | CSO | N/a | N/a | 4.75 | 11 | 100%
Anglian Water | Woodbridge Creek FM STW | ASETS/1250/V002 | CSO | Deben | N/a | 0 | 0 | 100%
Anglian Water | Woodbridge Deben Rd OV | AW4TS1417/V001 | CSO | Deben | N/a | 17.6667 | 40 | 98.52%
Anglian Water | Woodbridge - Quayside SPS | ASETS/4030/1403/V001 | CSO | Deben | N/a | 3.6333 | 10 | 100%
Anglian Water | Woodbridge - Station road | ASETS/16180/V001 | CSO | Deben | N/a | 9.6 | 8 | 100%

## EDM2 Year5
EDM Return for Anglian Water Annual 2020
Period selected from 01/04/2020 to 31/12/2020
Water Company Name | Site Name | Permit No. | Activity Reference (if more than one discharge) on permit | Shellfishery (Only populate for storm overflows that have Shellfish water EDM requirements) | Bathing Beach (Only populate for storm overflows that have bathing water EDM requirements) | Total Duration (hours) of all spills prior to processing through 12-24 hour counting method | Counted spills using 12-24hr counting method | % of reporting period EDM operational | Comments
Anglian Water | AKELEY (EX STW) SP | AWCNF417/10279/V001 | CSO | N/a | N/a | 141 | 18 | 100%
Anglian Water | ARTHINGWORTH TPS | AWNNF13783/V001 | CSO | N/a | N/a | 635.25 | 49 | 100% | Under investigation
Anglian Water | ASHWELL STW | AW1NF2723v002 | CSO | N/a | N/a | 2 | 2 | 100%
Anglian Water | ATTLEBOROUGH STW | AECNF/1004/V003 | CSO | N/a | N/a | 13.75 | 6 | 100%
Anglian Water | BALSHAM STW | ASCNF2051/V001 | CSO | N/a | N/a | 120.25 | 16 | 100%
Anglian Water | BARLEY STW | AW1NF1250/V002 | CSO | N/a | N/a | 11 | 15 | 99.98%
Anglian Water | BARNETBY-FERNERY LA TPS | AW3NFF763/V001 | CSO | N/a | N/a | 0.25 | 1 | 99.99%
Anglian Water | BARNHAM BROOME-MILL ROAD SM | AEENF2470/V001 | CSO | N/a | N/a | 334.5 | 24 | 100%
Anglian Water | BARNWELL TPS | AWNNF2128A | CSO | N/a | N/a |  |  |  | NPS have not yet issued a CSO condition under TDC project
Anglian Water | BARROW STW | ASCNF10281v001 | CSO | N/a | N/a | 640 | 36 | 100%
Anglian Water | BARTON-FLEETGATE TPS | AW3TS307/V002 | CSO | N/a | N/a | 34.5 | 33 | 100%
Anglian Water | BECCLES-CAXTON SPTS GRND OV | ASENF91783/10090/V001 | CSO | N/a | N/a | 5 | 1 | 100%
Anglian Water | BEDFIELD-CROWN LA SP | ASENF/19720/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | BENEFIELD STW | AW5NF5217B | CSO | N/a | N/a | 239.25 | 137 | 99.94% | Operational issue under investigation
Anglian Water | BLACKMORE-THE GREEN SP | AW2NFE01178/V001 | CSO | N/a | N/a | 69.75 | 12 | 100%
Anglian Water | BLAKESLEY TPS | AW1NF1057/V001 | CSO | N/a | N/a | 0 | 0 | 11.82% | Under investigation
Anglian Water | BOCKING-BRADFORD BRG (NEW) TPS | AW2NFE08765 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | BOXFORD STW | ASENF/1023/V002 | CSO | N/a | N/a | 215.75 | 16 | 100%
Anglian Water | BOZEAT STW | AW5NF421E | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | BRACKLEY-BRIDGE ST SSO | AW1NF1017 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | BRACKLEY (EX STW SITE) TPS | AWCNF537/10460/V001 | CSO | N/a | N/a | 41.75 | 19 | 100%
Anglian Water | BRACKLEY STW (NEW) | AWCNF10455/V003 | CSO | N/a | N/a | 148.75 | 16 | 100%
Anglian Water | BRIGG-SUNNINGDALE AV TPS | ANNNF3561/13486/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | BURTON LATIMER-HIGHAM ROAD SSO | AW5NF1825/V001 | CSO | N/a | N/a | 39 | 26 | 100%
Anglian Water | BURWELL STW | AW1NF1016 | CSO | N/a | N/a | 0.5 | 2 | 100%
Anglian Water | CANVEY-CHAMPLAIN AVE SP | ASETS2195/V003 | CSO | N/a | N/a | 1.25 | 1 | 100%
Anglian Water | CANVEY-HIGH ST SP | AW2NFE12084/V001 | CSO | N/a | N/a | 82.5 | 8 | 100%
Anglian Water | CAPEL ST MARY-PARKINS CL YD SP | ASENF2525/V003 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | CASTLE HEDINGHAM-QUEEN ST OV | EPR/NB3993AQ/V001 | CSO | N/a | N/a | 8.75 | 2 | 99.99%
Anglian Water | CATWORTH-HOSTEL STW | AWCNF10528C | CSO | N/a | N/a | 144.5 | 18 | 100%
Anglian Water | CHAPEL TPS | AECNF3114/11098/V001 | CSO | N/a | N/a | 0 | 0 | 85.17% | Under investigation
Anglian Water | CHATTERIS-HUNTINGDON RD OV | AECNF/10512/V003 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | CHEDBURGH STW | ASCNF1041v001 | CSO | N/a | N/a | 0.25 | 1 | 100%
Anglian Water | CHELSWORTH-CAKEBRIDGE LA SP | AW2NFE17472/V001 | CSO | N/a | N/a | 72.75 | 6 | 100%
Anglian Water | CHELVESTON-WATER LANE SP | AWNNF2203/V003 | CSO | N/a | N/a | 184 | 20 | 100%
Anglian Water | CHIPPENHAM STW | AW1NF482/V001 | CSO | N/a | N/a | 35.75 | 9 | 100%
Anglian Water | CLAYDON- IPSWICH RD |  | CSO | N/a | N/a | 0.02 | 1 | 93.67%
Anglian Water | CLAYPOLE-WELFEN LA TPS | ANNNF3251/13391/V001 | CSO | N/a | N/a | 13.75 | 5 | 100%
Anglian Water | CLIPSTON TPS | AWNNF1269/1 | CSO | N/a | N/a | 104.25 | 15 | 100%
Anglian Water | CODDENHAM-BLACKSMITHS LA TPS | ASENF2147/V003 | CSO | N/a | N/a | 17.75 | 5 | 100%
Anglian Water | COLCHESTER-BOURNE MILL OV | ASENF1720/V003 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | COLCHESTER-EAST BR (EAST)OV | ASETS1736/V003 | CSO | N/a | N/a | 53.75 | 143 | 92.92% | Possible SOAF investigation (Storm Overflow Assesment Framework) with EA agreement
Anglian Water | COLCHESTER-SHEARWATER MEWS OV | ASENF4129/19250/V001 | CSO | N/a | N/a | 0 | 0 | 95.06%
Anglian Water | COLD ASHBY SSO | AWNNF4191/13917/V001 | CSO | N/a | N/a | 4.75 | 10 | 100%
Anglian Water | CONINGTON-FEN DRAYTON RD SP | ASCNF43/10386/V001 | CSO | N/a | N/a | 128 | 6 | 100%
Anglian Water | COTTESMORE STW | AW5NF299D | CSO | N/a | N/a | 200.5 | 11 | 100%
Anglian Water | COVENEY-SCHOOL LANE SP | AECNF766/11067/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | COVENEY STW | AW1NF458 | CSO | N/a | N/a | 56 | 26 | 99.99%
Anglian Water | CRANSLEY (EXSTW) PS | AWNNF3689/13598/V001 | CSO | N/a | N/a | 50.25 | 4 | 100%
Anglian Water | DEEPINGS STW | ANNNF13012/V003 | CSO | N/a | N/a | 87.75 | 12 | 100%
Anglian Water | DICKLEBURGH-RECTORY RD STW | AEENF2055v001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | DISS-MOUNT ST OV | AW4NF929X/1 | CSO | N/a | N/a | 455 | 158 | 99.99% | Catchment investigation underway
Anglian Water | DOWNHAM MARKET-THE HYTHE SP | AECNF10447/V001 | CSO | N/a | N/a | 54 | 24 | 100%
Anglian Water | DULLINGHAM STW | AECNF10273v001 | CSO | N/a | N/a | 139.25 | 28 | 100%
Anglian Water | DUNHOLME STW | ANNNF10274v001 | CSO | N/a | N/a | 78 | 13 | 100%
Anglian Water | EAGLE SP | ANNNF3425/13427/V001 | CSO | N/a | N/a | 2.5 | 1 | 100%
Anglian Water | EARLS COLNE-CHURCH HILL #1 OV | AW2NFE/03265/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | EARLS COLNE-CHURCH HILL #3 OV | ASENF/16138/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | EARLS COLNE-COLCHESTER RD TPS | ASENF487/10322/V001 | CSO | N/a | N/a | 1 | 1 | 99.66%
Anglian Water | EAST HARLING STW | AECNF1062F/1 | CSO | N/a | N/a | 123.5 | 12 | 100%
Anglian Water | EASTON MAUDIT STW | AWNNF328013532v | CSO | N/a | N/a | 523.5 | 51 | 100% | Possible SOAF investigation (Storm Overflow Assesment Framework) with EA agreement
Anglian Water | E HANNINGFIELD-OLD CHRCH RD SP | AW2NFE03174/V001 | CSO | N/a | N/a | 46.25 | 8 | 100%
Anglian Water | EIGHT ASH GREEN-FORD ST TPS | ASENF3756 | CSO | N/a | N/a | 774 | 60 | 99.91% | Operational issue under investigation
Anglian Water | EIGHT ASH GREEN-HEATHFIELDS SP | ASENF2371/V003 | CSO | N/a | N/a | 7.5 | 4 | 50.36% | EDM Monitor issue now resolved
Anglian Water | ELMSTEAD-HOLLY WY THTCHRS D SP | ASENF2389/V003 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | ELMSWELL STW | ASCNF1065V001 | CSO | N/a | N/a | 306 | 35 | 99.92%
Anglian Water | ELSWORTH-ROGERS CL SP | AWCNF3519/11472/V001 | CSO | N/a | N/a | 74.5 | 7 | 100%
Anglian Water | ERPINGHAM-CALTHORPE BRIDGE SM | AW4NF1913/V001 | CSO | N/a | N/a | 238.75 | 28 | 100%
Anglian Water | ESSENDINE TPS | AW5NF5257/V001 | CSO | N/a | N/a | 186.25 | 10 | 100%
Anglian Water | EVENLEY STW | AWCNF2056B | CSO | N/a | N/a | 177.25 | 17 | 100%
Anglian Water | EVERDON STW | AWNNF3372/13345/V001 | CSO | N/a | N/a | 326.75 | 69 | 100% | Changed to alternative monitor type, now resolved
Anglian Water | EYE-HOXNE RD STW | AW4NF64X/V003 | CSO | N/a | N/a | 418.25 | 33 | 94.59%
Anglian Water | EYE-KINGS BR LOWGATE ST TPS | ASENF2283/V003 | CSO | N/a | N/a | 12.75 | 2 | 100%
Anglian Water | EYE-PETERBOROUGH ROAD SP | AWNNF2804A | CSO | N/a | N/a |  |  |  | NPS have not yet issued a CSO condition under TDC project
Anglian Water | FELSTED STW | AW2NF911C | CSO | N/a | N/a | 204.5 | 22 | 100%
Anglian Water | GRANBOROUGH-BATES CLOSE TPS | AWCNF3199/11350/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | GRASBY STW INLET OV | ANNNF2329/V002 | CSO | N/a | N/a | 34.75 | 12 | 100%
Anglian Water | GREAT EASTON STW (LEICS) | AW5NF/768/V002 | CSO | N/a | N/a | 717.75 | 62 | 100% | Operational issue resolved, under further investigation
Anglian Water | GRIMSBY RIBY ST.PS O.F | AW3TS226/227D | CSO | N/a | N/a | 36.25 | 10 | 100%
Anglian Water | GRIMSCOTE SP | AW5NF177/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | GRIMSTON STW | AECNF948v001 | CSO | N/a | N/a | 917.5 | 53 | 100% | Catchment investigation underway
Anglian Water | GT BADDOW-BRAMSTON CL OV | ASENF3030/12075/V001 | CSO | N/a | N/a | 31.5 | 14 | 100%
Anglian Water | GT COATES-STATION RD SP | ANNNF3505/13457/V001 | CSO | N/a | N/a | 1.5 | 3 | 100%
Anglian Water | GT EASTON-BRIDGEFOOT TPS | ASENF646/10513/V001 | CSO | N/a | N/a | 51.75 | 6 | 100%
Anglian Water | GT OAKLEY-SPARROWS CNR SP | AW2NFE02784/V001 | CSO | N/a | N/a | 51 | 17 | 100%
Anglian Water | GT WALTHAM-HOWE ST SP | ASENF2394/V003 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | GT WHELNETHAM STW | ASCNF/2062/V005 | CSO | N/a | N/a | 239.75 | 15 | 100%
Anglian Water | GT YELDHAM-POOLE ST SM | EPR/NB3992WR/V001 | CSO | N/a | N/a | 146.25 | 19 | 100%
Anglian Water | HADDENHAM-NEW TOWN RD SP | AECNF2494/V002 | CSO | N/a | N/a | 57.25 | 9 | 100%
Anglian Water | HADDENHAM STW | AECNF1089v002 | CSO | N/a | N/a | 170 | 20 | 100%
Anglian Water | HALSTEAD STW | AW2NF/524/V004 | CSO | N/a | N/a | 419.5 | 41 | 100%
Anglian Water | HARDINGSTONE SEWERAGE SCHEME (AKA Delapre Golf course) | AW5NF71 | CSO | N/a | N/a | 115 | 56 | 99.93% | Under investigation
Anglian Water | HARDWICK MEADOWS FIELD SSO | AW5NF2030/1 | CSO | N/a | N/a | 25.75 | 20 | 99.72%
Anglian Water | HARPOLE-NORTHAMPTON RD SSO | AWCNF4018/13665/V001 | CSO | N/a | N/a | 33 | 16 | 97.84%
Anglian Water | HATLEY ST GEORGE STW | ASCNF472A | CSO | N/a | N/a | 1572.25 | 70 | 100% | Operational issue now resolved
Anglian Water | HAWKWELL-RECTORY RD HAWKWELL | AW2NFE10166 | CSO | N/a | N/a | 0 | 0 | 99.7%
Anglian Water | HELMDON TPS | AW1NF/223/V001 | CSO | N/a | N/a | 340.5 | 27 | 100%
Anglian Water | HEMSWELL R A F STW | ANNNF2068B | CSO | N/a | N/a | 205.75 | 13 | 96.84%
Anglian Water | HOLTON-TETNEY LA TPS | AW3NF443/V001 | CSO | N/a | N/a | 0 | 0 | 98.43%
Anglian Water | HULLBRIDGE-KESWICK AVENUE | AW2NFE04179/V001 | CSO | N/a | N/a | 0 | 0 | 99.95%
Anglian Water | INGRAVE-PS | ASENF1109/V001 | CSO | N/a | N/a | 22.75 | 7 | 100%
Anglian Water | Irthlingborough Lime St CSO | EPR/NB3691EW/V001 | CSO | N/a | N/a | 26.25 | 24 | 99.87%
Anglian Water | KETTERING-VALLEY WALK SSO | AW5NF1831/V001 | CSO | N/a | N/a | 651 | 62 | 99.99% | Under investigation
Anglian Water | KIBWORTH-RAILWAY BRIDGE SSO | AW5NF1869/V001 | CSO | N/a | N/a | 2.75 | 6 | 99.99%
Anglian Water | KIBWORTH-WESTSIDE SSO | AW5NF1873 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | KINGS LYNN-SAMPHIRE PLACE SP | AECNF680/10468/V001 | CSO | N/a | N/a | 2 | 5 | 100%
Anglian Water | KNAPWELL-SP | AWCNF3523/11492/V001 | CSO | N/a | N/a | 42.75 | 3 | 100%
Anglian Water | KNOSSINGTON STW | AWNNF3066(SSO) | CSO | N/a | N/a | 495 | 46 | 100% | Operational issue under investigation
Anglian Water | LACEBY STW | ANNNF1490/V001 | CSO | N/a | N/a | 309.25 | 45 | 99.86%
Anglian Water | LAXFIELD STW | ASENF3088 | CSO | N/a | N/a | 119.5 | 26 | 100%
Anglian Water | LEASINGHAM-MOOR LA TPS | AW3NFF1039B/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | LINCOLN-OUTER CIRCLE RD SSO | ANNNF90835/10242/V001 | CSO | N/a | N/a | 1.25 | 3 | 89.5% | Under investigation
Anglian Water | LINCOLN-SINCIL BANK SSO | AW3NF833/V001 | CSO | N/a | N/a | 2988.5 | 126 | 100% | Reporting logic resolved
Anglian Water | LITTLE BYTHAM-STATION RD SSO | AW5NF1812/V001 | CSO | N/a | N/a | 60.75 | 9 | 100%
Anglian Water | LITTLE DOWNHAM PS | AW1NF445 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | LITTLE DOWNHAM STW | AECNF10119B | CSO | N/a | N/a | 214.75 | 34 | 100%
Anglian Water | LITTLEPORT STW | AECNF675/10518/V006 | CSO | N/a | N/a | 207.75 | 26 | 100%
Anglian Water | LITTLE WRATTING SPS | AW2NFE02280/V001 | CSO | N/a | N/a | 191 | 20 | 100%
Anglian Water | LOWESTOFT-NORWICH RD #2 SO | ASENF16992/1 | CSO | N/a | N/a | 0.75 | 3 | 99.98%
Anglian Water | LOWESTOFT-NORWICH RD SO | ASETS16992 | CSO | N/a | N/a | 0.75 | 3 | 99.98%
Anglian Water | LOWESTOFT-ROTTERDAM RD #1 SO | EPR/LB3996NV/V001 | CSO | N/a | N/a | 0.25 | 1 | 98.94%
Anglian Water | LOWESTOFT-ST PETERS ST #1 SO | EPR/MB3495AV/V001 | CSO | N/a | N/a | 7.5 | 21 | 96%
Anglian Water | LT DOWNHAM-CALIFORNIA SSO | AECNF3545/11457/V001 | CSO | N/a | N/a | 5.5 | 9 | 100%
Anglian Water | LT WALTHAM-CHATHAM GN SP | ASENF2200/V003 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | MANEA-TOWN LOTS STW | AECNF11429/V002 | CSO | N/a | N/a | 206 | 28 | 100%
Anglian Water | MARKET HARBOROUGH STW | AW5NF739/V002 | CSO | N/a | N/a | 578.25 | 51 | 100% | Possible SOAF investigation (Storm Overflow Assesment Framework) with EA agreement
Anglian Water | MARSTON-STATION ROAD TPS | AWCNF3168/11325/V001 | CSO | N/a | N/a | 4.25 | 1 | 100%
Anglian Water | MEARS ASHBY MAIN SP | AW5NF455/V001 | CSO | N/a | N/a | 1.25 | 2 | 100%
Anglian Water | MENDLESHAM-TPS | ASENF2457A | CSO | N/a | N/a |  |  |  | NPS have not yet issued a CSO condition under TDC project
Anglian Water | MEPAL STW | AECTF11049C | CSO | N/a | N/a | 106.5 | 18 | 100%
Anglian Water | METHERINGHAM STW | AW3NFF821/V001 | CSO | N/a | N/a | 199.5 | 34 | 100%
Anglian Water | MIDDLETON STW (NORTHANTS) | AW5NF/5226C/V001 | CSO | N/a | N/a | 6 | 5 | 100%
Anglian Water | MOLESWORTH STW | AWCNF11400D | CSO | N/a | N/a | 166.25 | 13 | 100%
Anglian Water | NASH-REAR OF CHURCH SP | AWCNF2735/V003 | CSO | N/a | N/a | 10.75 | 1 | 100%
Anglian Water | Newmarket STW SSO | AW1NF2476/V001 | CSO | N/a | N/a | 67.25 | 12 | 100%
Anglian Water | NEWMARKET STW - CSO | AW1NF2476/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | N KELSEY-BRIGG RD TPS | ANNNF2500/V003 | CSO | N/a | N/a | 15.25 | 12 | 100%
Anglian Water | NORTHAMPTON - BERRY LANE CSO | AW5NF1815/V001 | CSO | N/a | N/a | 4.25 | 6 | 93.67%
Anglian Water | NORTH HYKEHAM STW | ANNNF1153/V001/1 | CSO | N/a | N/a | 133 | 7 | 100%
Anglian Water | NORTON STW (NORTHANTS) | AW5NF247E | CSO | N/a | N/a | 95.75 | 22 | 100%
Anglian Water | OLDHURST STW | AWCNF1160C/V002 | CSO | N/a | N/a | 633.5 | 49 | 100% | Under investigation
Anglian Water | ONEHOUSE-NORTHFIELD EST TPS | ASENF2508A | CSO | N/a | N/a |  |  |  | NPS have not yet issued a CSO condition under TDC project
Anglian Water | OUNDLE-GLAPTHORN RD SP | AWNNF2321A | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | OVER-FEN ROAD SO SSO | AW1NF1412/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | OVER STW | ASCNF1162/V002 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | PAPWORTH EVERARD STW | AW1NF1003/V003 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | PAULERSPURY-CUTTLE MILL SP | AW1NF829 | CSO | N/a | N/a | 23.75 | 5 | 100%
Anglian Water | PERTENHALL STW | AW1NF2724B | CSO | N/a | N/a | 3547 | 165 | 100% | Operational issue now resolved
Anglian Water | PETBORO-WERRTON FENBRIDGE SP | AWNNF2805/V003 | CSO | N/a | N/a | 1 | 2 | 100%
Anglian Water | PETERBOROUGH ULLSWATER AVE MM | AW5NF1795/V001 | CSO | N/a | N/a | 7.25 | 1 | 100%
Anglian Water | PITSFORD SP | AWNNF3676/13563/V001 | CSO | N/a | N/a | 17 | 8 | 100%
Anglian Water | PLESHEY-FORD END SP | ASENF2311/V003 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | POLEBROOK TPS | AWNNF2534A | CSO | N/a | N/a |  |  |  | NPS have not yet issued a CSO condition under TDC project
Anglian Water | POTTERSBURY-CHURCH END SO- SSO | AW1NF1126/V001 | CSO | N/a | N/a | 37.5 | 5 | 99.3%
Anglian Water | POTTON-ROYSTON STREET SSO | AWCNF3246/11391/V002 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | RAMSDEN HEATH-HEATH RD SP | ASCNF2369A | CSO | N/a | N/a |  |  |  | NPS have not yet issued a CSO condition under TDC project
Anglian Water | RAMSEY-BODSEY TPS | AWCNF2779/V003 | CSO | N/a | N/a | 16.25 | 3 | 100%
Anglian Water | RAUNDS-BROOK ST SSO | AW5NF530 | CSO | N/a | N/a | 443.5 | 34 | 93.14%
Anglian Water | RAUNDS-ROTTEN ROW/HIGH STREET | AW5NF645/V001 | CSO | N/a | N/a | 0 | 0 | 98.34%
Anglian Water | RAYLEIGH-BARTLETTES RD SP | ASENF2130A | CSO | N/a | N/a |  |  |  | NPS have not yet issued a CSO condition under TDC project
Anglian Water | RAYLEIGH-EAST STW | ASENF1172/G | CSO | N/a | N/a | 32.5 | 4 | 100%
Anglian Water | RAYLEIGH-WEST STW | AW2TSE12870G | CSO | N/a | N/a | 1996.25 | 99 | 99.57% | Proposed SOAF investigation (Storm Overflow Assesment Framework) with EA agreement
Anglian Water | RAYLEIGH-WYBURNS AVE SP | AW2NFE10060 | CSO | N/a | N/a | 3 | 2 | 100%
Anglian Water | RAYNE-TPS | ASENF3974/15794/V001 | CSO | N/a | N/a | 27.5 | 7 | 100%
Anglian Water | REEPHAM-KENNEL LA/CLOUGH HIL | ANNNF1641/V003 | CSO | N/a | N/a | 0 | 0 | 99.13%
Anglian Water | REEPHAM STW (LINCS) | AW3NFF752 | CSO | N/a | N/a | 83.25 | 15 | 100%
Anglian Water | REEPHAM STW (NORFOLK) | AEENF2556A | CSO | N/a | N/a |  |  |  | NPS have not yet issued a CSO condition under TDC project
Anglian Water | ROCHFORD-DORIE AVE & ASHINGD | AW2NFE03369 | CSO | N/a | N/a | 0 | 0 | 88.07% | Under investigation
Anglian Water | ROCHFORD-SCOTTS HALL RD SP | ASENF2585A | CSO | N/a | N/a |  |  |  | NPS have not yet issued a CSO condition under TDC project
Anglian Water | ROTHERSTHORPE SP | AW5NF113/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | ROUGHAM-KINGSHALL GRN SP | AW1NF1273/V001 | CSO | N/a | N/a | 12.25 | 2 | 100%
Anglian Water | ROYSTON STW | AW1NF/2535/V002 | CSO | N/a | N/a | 27.5 | 3 | 43.8% | EDM Monitor issue now resolved
Anglian Water | RUNWELL-BROCK HILL OVERFLOW | ASENF3152/12108/V001 | CSO | N/a | N/a | 0 | 0 | 99.97%
Anglian Water | RUNWELL-DOWHNAM RD OVERFLOW | ASENF3151/12107/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | RUNWELL-TPS | AW2NFE03883/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | RUSHDEN-COURT ESTATE SP | AWCNF2238A | CSO | N/a | N/a |  |  |  | NPS have not yet issued a CSO condition under TDC project
Anglian Water | RUSHDEN-DUCK STREET MS | AW5NF672/V001 | CSO | N/a | N/a | 227.75 | 32 | 99.92%
Anglian Water | RUSKINGTON-MH0102 MANOR ST SSO | ANNNF1750/V003 | CSO | N/a | N/a | 0.75 | 2 | 100%
Anglian Water | SANDY STW | AW1NF/759/V002 | CSO | N/a | N/a | 1.25 | 1 | 100%
Anglian Water | SAWSTON STW | ASCNF1186/V001 | CSO | N/a | N/a | 149.75 | 11 | 100%
Anglian Water | SCOTHERN TPS | ANNNF3565/13483/V001 | CSO | N/a | N/a | 21.75 | 6 | 100%
Anglian Water | SHENFIELD AND HUTTON STW | ASENF10453/V004 | CSO | N/a | N/a | 350.25 | 45 | 100%
Anglian Water | SHIPDHAM-PARKLANDS AVENUE CSO | AEENF3669/12394/V001 | CSO | N/a | N/a | 107.75 | 38 | 99.98%
Anglian Water | SHOTLEY-OVERHALL FM STW | ASETS1532D | CSO | N/a | N/a | 0.25 | 1 | 100%
Anglian Water | SIBSEY STW | ANNNF10527v001 | CSO | N/a | N/a | 166.25 | 11 | 99.88%
Anglian Water | SKEGNESS-RICHMOND DR TPS | ANNNF3615/13482/V001 | CSO | N/a | N/a | 96.5 | 7 | 100%
Anglian Water | SKELLINGTHORPE STW | ANNNF1192C | CSO | N/a | N/a | 40.25 | 4 | 100%
Anglian Water | S KELSEY-SOUTH SP | ANNNF2598A | CSO | N/a | N/a |  |  |  | NPS have not yet issued a CSO condition under TDC project
Anglian Water | S Killingholme - Eastfield Rd | ANNNF13924/V001 | CSO | N/a | N/a | 2311.75 | 118 | 99.99% | Operational issue now resolved
Anglian Water | S. Killingholme Town Street CSO | ANNNF4178/13926/V001 | CSO | N/a | N/a | 3 | 6 | 100%
Anglian Water | SNITTERBY SP | ANNNF90756/10111/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | SOUTHEND - 21 - 27 SHAKESPEARE AVENUE | AW2NFE18768 | CSO | N/a | N/a | 0.25 | 1 | 99.98%
Anglian Water | SOUTHEND STW | S/WR340/V001 | CSO | N/a | N/a | 65.75 | 23 | 99.96%
Anglian Water | SOUTHERY-LITTLE LONDON SP | AECNF499/10369/V001 | CSO | N/a | N/a | 8.25 | 8 | 100%
Anglian Water | SOUTHERY-MILL DROVE STW | AECNF499/10369/V001 | CSO | N/a | N/a | 365.75 | 22 | 100%
Anglian Water | SOUTHMINSTER-16 HALL RD OV | ASENF307/10414/V001 | CSO | N/a | N/a | 263.25 | 41 | 99.83%
Anglian Water | SOUTHMINSTER-BURNHAM RD OV | ASENF306/10329/V002 | CSO | N/a | N/a | 30.5 | 64 | 99.81% | Under investigation
Anglian Water | SOUTHMINSTER-DEVONSHIRE RD SP | ASENF2251A | CSO | N/a | N/a |  |  |  | NPS have not yet issued a CSO condition under TDC project
Anglian Water | SPRATTON TPS | AWNNF2605/V003 | CSO | N/a | N/a | 2.5 | 1 | 100%
Anglian Water | STALHAM-MILL ROAD TPS | AW4NF1917/12216/V001 | CSO | N/a | N/a | 15.5 | 7 | 99.97%
Anglian Water | STAMFORD - RUTLAND TERRACE | AWNNF4305 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | STANTON STW | ASCNF1208D | CSO | N/a | N/a | 106.25 | 14 | 100%
Anglian Water | Steeple Bumpstead Blois Rd TPS | AW2NFE15068/3 | CSO | N/a | N/a | 28.5 | 8 | 100%
Anglian Water | Steeple Bumpstead Lilley TPS | AW2NFE15068/2 | CSO | N/a | N/a | 43.5 | 5 | 100%
Anglian Water | Steeple Bumpstead WRC | ASENF1543B | CSO | N/a | N/a | 3.75 | 6 | 100%
Anglian Water | STEEPLE CLAYDON TPS | AWCNF4095/11966/V001 | CSO | N/a | N/a | 68.75 | 11 | 100%
Anglian Water | STIFFORD-CORRAN WAY SP | AW2NFE02783/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | ST IVES-ILEX ROAD TPS | AWCNF2782A | CSO | N/a | N/a |  |  |  | NPS have not yet issued a CSO condition under TDC project
Anglian Water | ST IVES-MEADOW LANE PS | AWCNF3196/11339/V001 | CSO | N/a | N/a | 5821.75 | 308 | 100% | Changed to alternative monitor type, now resolved
Anglian Water | STOKE FERRY STW | AWCNF11338D | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | ST OSYTH STW | AW2NFE08562H | CSO | N/a | N/a | 0.25 | 1 | 99.97%
Anglian Water | STOTFOLD-BROOK END SP | AWCNF93038/10216/V001 | CSO | N/a | N/a | 7.25 | 2 | 100%
Anglian Water | STOWMARKET-PRENTICE RD TPS | ASENF2538A | CSO | N/a | N/a |  |  |  | NPS have not yet issued a CSO condition under TDC project
Anglian Water | STOWMARKET STW | ASENF1211v002 | CSO | N/a | N/a | 228 | 17 | 100%
Anglian Water | STRADBROKE OLD STW SP | ASENF3038/12059/V001 | CSO | N/a | N/a | 248 | 22 | 100%
Anglian Water | STRETHAM-OFF BERRY GREEN SP | AECNF10544C | CSO | N/a | N/a | 34.5 | 10 | 100%
Anglian Water | STRETHAM-OFF NEWMARKET RD TPS | AECNF10543/V001 | CSO | N/a | N/a | 257 | 25 | 100%
Anglian Water | STRETHAM STW | AECNF1213B | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | STRETTON SP | AWNNF2639A | CSO | N/a | N/a |  |  |  | NPS have not yet issued a CSO condition under TDC project
Anglian Water | STUKELEY-LOW ROAD TPS | AWCNF2771/V003 | CSO | N/a | N/a | 644.75 | 53 | 100% | Operational issue under investigation
Anglian Water | STUNTNEY-LOWER STREET SP | AECNF3003/11072/V001 | CSO | N/a | N/a | 55.25 | 8 | 100%
Anglian Water | Sturmer Kedington Rd TPS | AW2NFE15068/1 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | STURTON BY STOW STW | ANNNF1215v001 | CSO | N/a | N/a | 100.75 | 14 | 100%
Anglian Water | SUDBURY-CORNARD RD SP | ASENF3546/12336/V001 | CSO | N/a | N/a | 1.25 | 4 | 100%
Anglian Water | SUTTON-STH OF THE ROW OV | AW1NF996/V001 | CSO | N/a | N/a | 164.75 | 21 | 99.97%
Anglian Water | SWARDESTON-THE COMMON TPS | AEENF2228/V003 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | THAXTED-PARK STREET | AW2NFE03679/V001 | CSO | N/a | N/a | 49.5 | 33 | 99.88%
Anglian Water | THETFORD-HAYLING PATH SP | AECNF778A/11042/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | THORNBY SP | AWNNF2672A | CSO | N/a | N/a |  |  |  | NPS have not yet issued a CSO condition under TDC project
Anglian Water | THORNDON-STANDWELL GN TPS | ASENF2673/V003 | CSO | N/a | N/a | 132 | 17 | 100%
Anglian Water | THORNEY STW | AW5NF361/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | THORRINGTON STW | AW2NFE02070G | CSO | N/a | N/a | 138.5 | 31 | 93.73%
Anglian Water | THURLEIGH-CHURCH END SP | AWCNF2676/V003 | CSO | N/a | N/a | 0 | 0 | 90.59%
Anglian Water | THURLTON-THE STREET TPS | AEENF2665/V003 | CSO | N/a | N/a | 46.75 | 7 | 100%
Anglian Water | TINGEWICK - FOUL SP | AWCNF3212/11346/V001 | CSO | N/a | N/a | 237.75 | 24 | 100%
Anglian Water | TIPTREE STW | AW2NFE04662/V1 | CSO | N/a | N/a | 743.75 | 47 | 100% | Possible SOAF investigation (Storm Overflow Assesment Framework) with EA agreement
Anglian Water | TODDINGTON-LUTON ROAD SSO | AW1NF2737/V001 | CSO | N/a | N/a | 2 | 8 | 98.67%
Anglian Water | TOLLESHUNT-D ARCY STW | ASENF1317B | CSO | N/a | N/a | 2.5 | 2 | 99.99%
Anglian Water | TWYFORD-SCHOOL LANE TPS | AW1NF514/V001 | CSO | N/a | N/a | 1.5 | 1 | 100%
Anglian Water | ULCEBY SKITTER SP | ANNNF3465/13431/V001 | CSO | N/a | N/a | 12.75 | 5 | 100%
Anglian Water | WAINFLEET STW | ANNNF10437C | CSO | N/a | N/a | 17.5 | 7 | 100%
Anglian Water | WALCOTT-THE DRIFT SP | ANNNF3428/13429/V001 | CSO | N/a | N/a | 71.75 | 21 | 100%
Anglian Water | WALGRAVE SP | AWNNF3218/13356/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | WALSHAM LE WILLOWS-CAUSEWY TPS | ASCNF10014/V001 | CSO | N/a | N/a | 106.5 | 32 | 100%
Anglian Water | WARBOYS-CHURCH STREET TPS | AWCNF890/11054/V001 | CSO | N/a | N/a | 11.25 | 3 | 100%
Anglian Water | WARDY HILL-WITCHAM ROAD SP | AECNF768A | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | WARMINGTON STW | AW5NF/96/V003 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | WATERBEACH STW | ASCNF/10357/V004 | CSO | N/a | N/a | 240.75 | 16 | 100%
Anglian Water | WATTON STW | AECNF/10530/V003 | CSO | N/a | N/a | 291.75 | 27 | 100%
Anglian Water | WEEDON BEC WEST STREET SSO | AW5NF65/2 | CSO | N/a | N/a | 6.75 | 2 | 100%
Anglian Water | WEEDON STW | AWNNF3070v002 | CSO | N/a | N/a | 131.5 | 21 | 100%
Anglian Water | WELLINGBOROUGH-CROYLAND GARD | AWNNF749A | CSO | N/a | N/a | 0.25 | 1 | 97.39%
Anglian Water | WELLINGBOROUGH-HATTON PARK SSO | AWNNF4110 | CSO | N/a | N/a | 23 | 9 | 99.16%
Anglian Water | WELLINGBOROUGH-ISE VALLEY TPS | AWNNF2405/V003 | CSO | N/a | N/a | 38 | 3 | 99.89%
Anglian Water | WELLINGBOROUGH-RAIL STATIONSSO | AW5NF311(4)A | CSO | N/a | N/a | 29.25 | 19 | 99.88%
Anglian Water | WELLINGBOROUGH-SHEPHERDS YAR | AW5NF1807/V001 | CSO | N/a | N/a | 0.25 | 1 | 99.89%
Anglian Water | WELLINGBOROUGH TPS | AW5NF589/V003 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | WELLS-FREEMAN ST OV | AEENF820/12015/V001 | CSO | N/a | N/a | 0 | 0 | 99.89%
Anglian Water | WELTON-LE-WOLD STW | AW3NFF1300/V001 | CSO | N/a | N/a | 0.75 | 2 | 100%
Anglian Water | WENTWORTH-COLLEGE FARM SP | AW1NF1000/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | WESTON BY WELLAND STW | AW5NF5224C | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | WEYBOURNE-BEACH LANE SP | AEENF/3679/V001 | CSO | N/a | N/a | 5.75 | 1 | 100%
Anglian Water | WHITE NOTLEY STW | AW2NF811v001 | CSO | N/a | N/a | 143.75 | 15 | 100%
Anglian Water | WHITTLESEY STW | AW5NF810/V002 | CSO | N/a | N/a | 618 | 36 | 91.21%
Anglian Water | WICKEN-DRURY LANE SP | AECNF797A | CSO | N/a | N/a | 183.25 | 13 | 100%
Anglian Water | WICKFORD STW | ASETS1322v001 | CSO | N/a | N/a | 220.75 | 16 | 100%
Anglian Water | WICKHAMBROOK-BROOK COTTS TPS | ASENF3638/12368/V001 | CSO | N/a | N/a | 1.25 | 2 | 99.98%
Anglian Water | WICKHAM SKEITH-TPS | ASENF2719A | CSO | N/a | N/a |  |  |  | NPS have not yet issued a CSO condition under TDC project
Anglian Water | WILBURTON STW | AECNF803/11021/V001 | CSO | N/a | N/a | 465.5 | 46 | 100% | Possible SOAF investigation (Storm Overflow Assesment Framework) with EA agreement
Anglian Water | WINTERTON-EARLSGATE SP | AW3NFF1044/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | WINTERTON-PARK ST 1 SSO | PR3NFF498 | CSO | N/a | N/a | 5.5 | 5 | 100%
Anglian Water | WISBECH-LYNN RD TPS | AW5TS799B/V001 | CSO | N/a | N/a | 46.75 | 12 | 100%
Anglian Water | WITCHFORD STW | AECNF1402v001 | CSO | N/a | N/a | 3 | 2 | 100%
Anglian Water | WITCHAM STW |  | CSO | N/a | N/a | 463.5 | 39 | 100%
Anglian Water | WITHAM STW | ASETS12105C | CSO | N/a | N/a | 230.25 | 16 | 100%
Anglian Water | WIVENHOE-PHILLIP RD OV | ASETS4128/19248/V001 | CSO | N/a | N/a | 83.75 | 9 | 98.65%
Anglian Water | WIVENHOE-THE FOLLY OV | ASETS4127/19247/V001 | CSO | N/a | N/a | 2970 | 135 | 98.42% | Under investigation
Anglian Water | WOBURN PS | AWCNF1249A | CSO | N/a | N/a | 389.5 | 30 | 100%
Anglian Water | WOLLASTON LONDON RD SSO | AW5NF2034/V001 | CSO | N/a | N/a | 20 | 22 | 95.3%
Anglian Water | WOODFORD-THE MOORINGS SP | AWNNF2736/V002 | CSO | N/a | N/a | 209 | 27 | 100%
Anglian Water | WOODHALL SPA STW TPS | ANNNF10217/V001 | CSO | N/a | N/a | 141 | 36 | 100%
Anglian Water | WOOLVERSTONE-MARINA TPS | ASETS724/V001 | CSO | N/a | N/a | 3.25 | 2 | 100%
Anglian Water | WRITTLE-LAWFORD LA SP | AW2NFE22969 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | WYMONDHAM-STATION RD SP | AEENF3358/12206/V001 | CSO | N/a | N/a | 0 | 0 | 100%
Anglian Water | WYMONDHAM STW | AW4NF/430X/V003 | CSO | N/a | N/a | 237.5 | 23 | 100%
Anglian Water | WYTON (RAF) STW | AWCNF11516v002 | CSO | N/a | N/a | 724 | 53 | 100% | Under investigation
Anglian Water | YARDLEY HASTINGS STW | AWNNF13310B | CSO | N/a | N/a | 557 | 53 | 99.98% | Under investigation
Anglian Water | YARDLEY HASTINGS WORKS SP | AWNNF3109/13311/V001 | CSO | N/a | N/a | 7 | 5 | 100%